# Power Operations Bulletin #98

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Added new section 2.2.4 “Remedial Action Plans.”

V2R23 – CN#136

| ### 2.2.4 Remedial Action Plans |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | A Remedial Action Plan is to relieve the loading on the Transmission Facility within 15 minutes. ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the 15-Minute Rating. The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within 15 minutes. |
| CAUTION | Remedial Action Plans are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. |
| 1 | - When RTCA shows a post-contingency overload and a Remedial Action Plan exists resolve it, - REVIEW the Remedial Action Plan with the associated Transmission Operator - Notify the Shift Supervisor of the anticipated actions. |
| 2 | If a Remedial Action Plan does not exist for this contingency and the Outage Notes do not provide a plan, REQUEST that Operations Engineering investigate development of a Remedial Action Plan for the anticipated insecure state. |
| 3 | If the contingency anticipated by the Remedial Action Plan takes place, - DIRECT implementation of the Remedial Action Plan RESPOND as quickly as possible to requests made by the Transmission Operator in accordance with the Remedial Action Plan. |
| 4 | If Post-Contingency loading approached the “15-Minute Rating,” utilize pre-contingency congestion management methods to keep the Post-contingency loading below the “15-Minute Rating.” |
| NOTE: | In RTCA, the “15-Minute Rating” and “LDSH” refer to the same rating. |