# Power Operations Bulletin #104

ERCOT has revised the Frequency Control Desk section of the Operating Procedure Manual.

Changes include adding new section entitled “Actions When Frequency Telemetry is Incorrect”, now Section 2.5.4.

| ### 2.5.4 Actions When Frequency Telemetry is Incorrect |  |
| --- | --- |
| ###### Purpose: | ###### To prevent the unnecessary deployment of Responsive Reserve due to incorrect telemetry frequency data. |
| 1 | When frequency reaches 59.91 HZ and responsive reserve is deployed, VERIFY that the frequency is correct by comparing the data from multiple sources. - Use the “Generation Telemetered Data” display and select “OPA Data from SCADA” |
| 2 | If the frequency is incorrect and below 59.91 HZ, stop the deployment of responsive reserve by selecting the “Unrequest All QSEs” button on the “ERCOT Responsive, Regulation, and SCE” (Responsive display). |
| 3 | If the frequency is incorrect, hold the present Regulation deployments. Depress and hold the “On” button and select “Monitor” to place the AGC in Monitor mode. This stops changing regulation deployments. Use the “ERCOT Responsive, Regulation, and SCE” (Regulation display). |
| 4 | - When the frequency telemetry is correct, enable the auto deployment of responsive reserve by selecting the “Request All QSEs” button on the “ERCOT Responsive, Regulation, and SCE” (Responsive display). |
| 5 | When the frequency telemetry is correct, enable deployments of regulation. Depress and hold the “On” button and select “Monitor” to allow regulation deployment changes based on system frequency. Use the “ERCOT Responsive, Regulation, and SCE” (Regulation display). |
| 6 | Make appropriate log entries in the Operator’ log. |

A copy of the procedure, Frequency Control Desk V2R13 – CN #143, is attached.