# ERCOT Operations Bulletin 200

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include updating section 2.4.3 “DFW Reactive Reserves.”

| ### 2.4.3 DFW Dynamic Reactive Reserves |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Note: | Based on the table below it is necessary to have a certain amount of dynamic reactive reserves in the DFW area at all times to avoid voltage collapse and maintain the system in the secure state. |
| 1 | If the spread sheet indicates that dynamic reactive reserves have fallen below the limit required based on the DFW load, initiate the following actions: - Have the TOs place all capacitors in the DFW area in service. - Have the TOs take all the reactors in the DFW area out of service. - Using Appendix 10, increase generation on the available units. - Bring additional DWF generation on-line. Units should be chosen from Appendix 10 based on response time and system requirements. The system operator may use his/her discretion regarding order and timing of the above actions. |
| 2 | If the dynamic reactive reserves do not return to the required amount after completing all of the recommended actions in step 1, issue a “Voltage Collapse” alert in the DFW area and call on Operations Support Engineers for assistance. |

| S. No | Load in DFW in MW | Required Reactive Reserve in MVAr |
| --- | --- | --- |
| 1 | 9000 | 900 |
| 2 | 10000 | 1000 |
| 3 | 11000 | 1100 |
| 4 | 12000 | 1200 |
| 5 | 13000 | 1300 |
| 6 | 14000 | 1400 |

A copy of the updated procedure, Transmission & Security Desk V3R53, is available at

http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.