# ERCOT Operations Bulletin 200

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include updating section 2.4.3 “DFW Reactive Reserves.”

| 2.4.3 DFW Dynamic Reactive Reserves |
| --- |
| Step # | Procedural Steps |
| Note: | Based on the table below it is necessary to have a certain amount of dynamic reactive reserves in the DFW area at all times to avoid voltage collapse and maintain the system in the secure state. |
| 1 | If the spread sheet indicates that dynamic reactive reserves have fallen below the limit required based on the DFW load, initiate the following actions: Have the TOs place all capacitors in the DFW area in service. Have the TOs take all the reactors in the DFW area out of service. Using Appendix 10, increase generation on the available units. Bring additional DWF generation on-line. Units should be chosen from Appendix 10 based on response time and system requirements. The system operator may use his/her discretion regarding order and timing of the above actions. |
| 2 | If the dynamic reactive reserves do not return to the required amount after completing all of the recommended actions in step 1, issue a “Voltage Collapse” alert in the DFW area and call on Operations Support Engineers for assistance. |

| S. No | Load in DFW in MW | Required Reactive Reserve in MVAr |
| --- | --- | --- |
| 1 | 9000 | 900 |
| 2 | 10000 | 1000 |
| 3 | 11000 | 1100 |
| 4 | 12000 | 1200 |
| 5 | 13000 | 1300 |
| 6 | 14000 | 1400 |

A copy of the updated procedure, Transmission & Security Desk V3R53, is available at

http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.