# Power Operations Bulletin #107

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include adding third note after step five and adding information regarding zonal limits in step, section 2.2.3.

| ### 2.2.3 Manage Transmission Limits, Constraints, and Congestion |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | MONITOR Transfer Limits against criteria defined on the following: - Transmission Limits to be Monitored report - Real Time Contingency Analysis as directed in section 2.1.2 - Outage Notes - Line Limits defined in the EMS (Network Limits) - Stability limits as described in section 2.2.3 - Written Instructions from ERCOT Management/Operations Engineering Zonal limits (CSC limits) will be enforced based upon the transmission limits to be monitored daily report. If real-time contingency analysis shows a post-contingency overload in response to the same contingency and monitored element shown as limiting a CSC on the daily report, then the RTCA results may be used as a basis of implementing zonal congestion relief. Otherwise only local techniques should be used. With the exception of CSC congestion, which is addressed in the paragraph above, if conflicts between these documents appear, then the Real Time Contingency Analysis should be used as the governing reference if it has solved within the last 10 minutes. If RTCA has not solved within the last 10 minutes then limits provided by Operations Engineering should govern. IF RTCA shows a post-contingency overload on a CSC, but the monitored element is a CRE and not reported on the daily limits sheet as the monitored limit for the CSC, use local methods to manage congestion. IF local techniques are unsuccessful, call Operations Support and use Zonal techniques to control the congestion. Use the MIS to post that Zonal techniques are being used to control congestion to RTCA values. IF a new Zonal limit is calculated by Operations Support, then use the MIS to post the new Zonal limit. Suggested verbiage for the MIS posting: Local congestion management techniques have been unsuccessful in controlling the CRE. “Contingency: Monitored Element. Zonal techniques will be utilized.” Reference Display: Real Time Transmission Constraint Limits – from POS, hit Ctrl D, type in RTL under SCADA application that appears, hit Call-up. |

Following Step 5

| NOTE: | A QSE may request a Settlements VDI when an OOME prevents them from meeting their Regulation or Responsive obligation. Issue this VDI only when a QSE makes a specific request. |
| --- | --- |

A copy of the procedure, Transmission & Security Desk V3R26, is attached.