# ERCOT Operations Bulletin 208

ERCOT has revised the Shift Supervisor Desk section of the Operating Procedure Manual.

Changes include incorporating new section 2.5.4 “Root Cause Analysis.”

A copy of the procedure is available at http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.

| ### Root Cause Analysis |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ###### The following events will trigger an investigation: - Possible violation of DCS Criteria - Frequency deviation of +/- .05 from scheduled frequency for greater than 30 minutes - High frequency events greater than 60.175 Hz. - “Held Intervals” - Incorrect procurement/deployment of NSRS - OC1 constraint operation that depletes the Balancing Market. - Operating actions outside of the Protocols, ERCOT Guides or Operating Procedures - Over constraining - A constraints that remains active with no corresponding congestion. - Anytime an OC1 that remains active for more than two intervals and it is below 90% of the limit - An OOME or VDI that with no corresponding congestion, import or voltage concerns The CSO may direct the investigation of other events not listed. |
| NOTE: | The “rule of thumb” is to ask why until the most basic cause of the problem is revealed. |
| 1 | When an event occurs, notify the CSO, Training Supervisor and Jeff Healy via e-mail that an investigation has been initiated. Include the event, time, duration and a summary of what occurred. |
| 2 | Preserve all data relevant to the event: - Market and power system data - Operational logs - Applicable graphs and charts |
| 3 | Evaluate the following conditions: - Resources - Software performance - Man – Machine interface - Procedures - Management directives - Training - Computer (hardware) performance - External Distracters - Control Room conditions - Market conditions - System conditions - Human Performance - QSE input and communication - TO input and communication - ERCOT internal support and communication - Shift communication and team work |
| 4 | A preliminary report is due within three days. The report should include: - A summary - The chain of events and/or decisions that produced the outcome. - The most basic root cause - Recommended steps to prevent future events from occurring. |
| 5 | Make three copies of the report. Forward two copies to the Training Supervisor. Keep one for the later discussion. |
| 6 | The Training Supervisor and Operations Engineering Support will review the report and meet with the Shift Supervisor. |
| 7 | A final report will be compiled by the Training Supervisor and forwarded to the CSO identifying the cause and recommending corrective action. |