# ERCOT Operations Bulletin 55

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

V2R14

| 2.2.2 Manage Transmission Limits, Constraints, and Congestion |  |  |
| --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |
| 3 | POST information electronically, or pass along in written form to affected Transmission Operators, a copy of updated transfer/transmission limits. (This may be done by posting on the Real-Time screen, or see Appendix 3 for a typical method of posting to the message board) Posted information shall contain the revised limit(s) and the period to which it/they apply. |  |
| 4 | ACTIVATE a constraint or OOME appropriate units when Real Time Contingency Analysis result shows that post contingency overloading exceeds 110% of emergency limits or Autotransformer loading exceeds 100% of emergency limits AND no Remedial Action Plan allowing higher post contingency loading exists. To determine what units will affect a post contingency overloaded element, look up the contingency-overload combination in the provided manual. The most positive shift factors indicate the units which REDUCING output will have the most beneficial effect in reducing post-contingency loading. The most negative shift factors indicate units which INCREASING output will have the most beneficial effect in reducing post-contingency loading. |  |
| NOTE: | If RTCA is unavailable, activate constraints or OOME units WHEN a monitored transfer limit has or is likely to exceed established reliability criteria. |  |
| NOTE: | IF a specific constraint is needed and does not exist, direct Ops Engineering to provide the constraint. |  |
| 5 | MONITOR Transmission System. IF – post contingency loading of transmission element remains above 110% (100% for autotransformers) continue. |  |

V2R15

| 2.2.2 Manage Transmission Limits, Constraints, and Congestion |  |  |
| --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |
| 3 | POST information electronically, or pass along in written form to affected Transmission Operators, a copy of updated transfer/transmission limits. (This may be done by posting on the Real-Time screen, or see Appendix 3 for a typical method of posting to the message board) Posted information shall contain the revised limit(s) and the period to which it/they apply. |  |
| 4 | ACTIVATE a constraint or OOME appropriate units when Real Time Contingency Analysis result shows that post contingency overloading exceeds 110% of emergency limits or Autotransformer loading exceeds 100% of emergency limits AND no Remedial Action Plan allowing higher post contingency loading exists. To determine what units will affect a post contingency overloaded element, look up the contingency-overload combination in the provided manual. The most positive shift factors indicate the units which REDUCING output will have the most beneficial effect in reducing post-contingency loading. The most negative shift factors indicate units which INCREASING output will have the most beneficial effect in reducing post-contingency loading. |  |
| NOTE | The requirements of step 5 are intended as a work-around until EMMS changes are made to accommodate the addition of “Resource Minimum Down Time” parameters into the Resource Plan as related to PRR454. |  |
| 5 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then issue a VDI to the QSE to disregard the OOME instruction for the appropriate intervals. |  |
| NOTE: | If RTCA is unavailable, activate constraints or OOME units WHEN a monitored transfer limit has or is likely to exceed established reliability criteria. |  |
| NOTE: | IF a specific constraint is needed and does not exist, direct Ops Engineering to provide the constraint. |  |
| 6 | MONITOR Transmission System. IF – post contingency loading of transmission element remains above 110% (100% for autotransformers) continue. |  |

- A copy of the Transmission & Security Desk V2R15 is attached.