# Power Operations Bulletin #133

ERCOT has revised the Transmission & Security Desk section of the Operating Procedure Manual.

Changes include new step six in section 2.2.3 “Manage Transmission Limits, Constraints, and Congestion.”

| 2.2.3 Manage Transmission Limits, Constraints, and Congestion |  |  |
| --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |
| 6 | When system conditions require one CT of a Combined Cycle Plant to be OOMEd off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |  |

A copy of the procedure, Transmission & Security Desk V3R32, is available at http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm.