# Power Operations Bulletin #227

CN# 297 – Western Area Action Plan for Voltage Support

## Effective Date:  December 6, 2005

## Expiration Date:  March 1, 2006

Renewing CN#279

Updated February 14, 2006

# Transmission& Security Desk

Purpose

Western Area Action Plan for Voltage Support

Procedure

At low load conditions all the reactors at MGSES, GRSES, ABMB, SARC, TWINBUTE, OKLA, MDLNE, ODEHV, BOMSW, RIOP and CMNSW need to be online and capacitors at SARC, HLSBR, UVALDE and UVLDES need to be offline.

To reduce high voltage in the Abilene Mulberry Creek or Fort Phantom areas do the following in the order if required

- Change the CPSES 345kV bus voltage to 343kV by reducing the voltage set point of CPSES

- Open the 345kV line from SARC to ABMB (close the CBs after opening the MOS to put the reactor back in service)

- Open the 345kV line from SARC to CMNSW