# ERCOT Operations Bulletin 258

ERCOT has revised the Transmission & Security Desk Procedure.  Revision includes incorporating new section 2.4.4.

| 2.4.4 VSAT Procedure |  |  |  |
| --- | --- | --- | --- |
| Step # |  |  |  |
| PURPOSE: | To monitor system voltages and to prevent voltage collapse. |  |  |
| NOTE: | Check VSAT every hour, or more frequently as necessary. |  |  |
| NOTE: | To contact VSAT support, check the board in the back of TCC for the on-call personnel. |  |  |
| 1. | Determine if VSAT has run in the last 80 minutes. Reference Display: Network Online Sequence If VSAT has not run in the last 80 minutes, contact VSAT support. |  |  |
| 2. | Confirm that VSAT is indicating either “Normal” or “Pending” status. NOTE: If VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status, contact VSAT support. Reference Display: Network Online Sequence |  |  |
| 3. | With VSAT in “Normal” status, determine if it indicates “Voltage Collapse”. Reference Display: VSAT Results Page NOTE: If VSAT does not indicate “Voltage Collapse”, no further action is required. |  |  |
| 4. | Determine if the Extra-Interface Limit pre-contingency value is less than the safety margin value located in the table below. Reference Display: Click “Details” button on VSAT Results Page Safety Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 175MW. O-DFW_L; 175MW. S-H_G; 175MW. S-H_L; 175MW. N-H_G; 175MW. N-H_L; 175MW. O-VALL_L; 75MW. NOTE: If it is not less than the safety margin value, no further action is required. |  |
| 5. | Check to see if the same contingency is unsolved in RTCA. Reference Display: Contingency Analyst Solution Results If so, call VSAT support and proceed to Step 7. If not, call VSAT Support for verification and weak bus information. |  |  |
| 6. | Determine if VSAT Support has verified the problem is real and they give feedback on weak bus information. NOTE: If not, no further action is required. |  |  |
| 7. | Once VSAT Support has verified the information, request the TDSP in the affected area turn on capacitor banks and turn off reactors near the weak busses. |  |  |
| 8. | Verify that the TDSP complied with the request. If so, rerun VSAT with new topology then determine if the Extra-Interface Limit pre-contingency is greater than the safety margin value located in the table below. Reference Displays: Network Online Sequence VSAT Results Page Click “Details” button on VSAT Results Page Safety Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 175MW. O-DFW_L; 175MW. S-H_G; 175MW. S-H_L; 175MW. N-H_G; 175MW. N-H_L; 175MW. O-VALL_L; 75MW. If it is greater than the safety margin value, no further action is required. If not, proceed to step 9. |  |
| 9. | OOME fast ramp generators to increase generation in weak bus area. |  |  |
| 10 | Rerun VSAT with new information. Reference Display: Network Online Sequence |  |  |
| 11. | Determine if the Extra-Interface Limit pre-contingency is greater than the safety margin value located in the table below. Reference Displays: VSAT Results Page Click “Details” button on VSAT Results Page Safety Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 175MW. O-DFW_L; 175MW. S-H_G; 175MW. S-H_L; 175MW. N-H_G; 175MW. N-H_L; 175MW. O-VALL_L; 75MW. NOTE: If it is greater than the safety margin value, no further action is required. If not, proceed to Step 12. |  |  |
| 12. | Determine if there are more units available in the affected area. If there are more units available in the affected area, repeat steps 9, 10, and 11. NOTE: If there are no more units available in the area, proceed to step 13. |  |  |
| 13. | Devise a mitigation plan. |  |  |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.