| 2.6.9 Provide Advanced Notice of Diminishing Responsive Reserve - ERCOT Operations Bulletin 280 ERCOT has revised the Frequency Control Desk section of the Operating Procedure Manual. Changes include updating steps 1-3, and step 3c. |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| NOTE: | Adjusted Responsive Reserve is equal to 93% of the sum of the Net Dependable Capability, or Resource Plan HOL, or the telemetered real time capability (whichever is less) of all online generating units’ that are capable of responding to system disturbances + 1150MW of LAAR. |
| 1 | IF Adjusted Responsive Reserve is equal to or less than 3300MW, issue an Operating Condition Notice (Refer to section 2.6.1 “Issue an Operating Notice (OCN)”). Typical script: “This is the ERCOT system operator. ERCOT is issuing an OCN to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 2 | IF Physical Adjusted Responsive Reserve is equal to or less than 3000MW, issue an Advisory (Refer to section 2.6.2 “Issue an Advisory”). Typical script: “This is the ERCOT system operator. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 3 | IF Adjusted Responsive Reserve is equal to or less than 2500MW, issue an Alert (Refer to section 2.6.3 “Issue an Alert”). Typical script: “This is the ERCOT system operator. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 3a | Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. |
| 3b | Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. |
| 3c | Utilize Non-Spin Reserve Services that can be deployed to increase Responsive reserves. |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.