# ERCOT Operations Bulletin 282

ERCOT has revised the Transmission & Security Desk Procedure.  Revision includes updating section 2.5.6 “Implementing EECP” and section 2.5.7 “Restoring EECP.”

| ### 2.5.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | In the absence of the Shift Supervisor, the Frequency Desk will implement applicable steps of the EECP. |
|  | CAUTION IF ERCOT frequency falls below 59.8 Hz THEN ERCOT SHOULD PROCEED to Step 4. IF ERCOT frequency falls below 59.5 Hz, THEN ERCOT SHALL PROCEED to Step 4 (Protocols 5.6.6.1; Operating Guide 4.5.3) |
| 1 | ISSUE EECP Step 1 under either of the following conditions: - ERCOT physical Responsive Reserve plus that amount of NSRS that has been deployed but has not ramped to specified output level falls below 2300 MW - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) (NOT in response to a generator trip unless sustained for more than 10 minutes) |
| 1.a | - ISSUE a voice message to Transmission Operators “ERCOT has implemented EECP Step 1,” using the hotline, if available. - POST via the ENS that “ERCOT implemented EECP Step 1.” |
| NOTE: | The Frequency Desk will issue a voice message, to all QSEs “ERCOT has implemented EECP Step 1. QSEs are to report when online available capacity is at risk due to adverse circumstance. QSEs are to update their Resource Plans when unexpected start-up delays occur or when ramp limitations are encountered. QSEs are to suspend all generating unit and resource testing. QSEs are to report back to the ERCOT System Operator when requested steps have been completed,” using the hotline if available. |
| 1.b | VERIFY the following actions have been completed: - That all QSEs have loaded RMR units to full capacity - All Non-Spin has been deployed - Uncommitted QSEs units available in the period of the emergency have been committed (e.g., OOMC) and loaded as necessary - Available North and East DC Tie capacity has been applied to the system as needed through an Emergency Assistance request to AEP |
| NOTE: | For more information on how AEP and ERCOT determine the available DC Tie capacity and coordinate Emergency Assistance over the DC Ties, refer to ERCOT Operating Procedure Manual, Direct Current Ties. |
| 1.c | ENSURE Southwest Power Pool Security Coordinator has been notified that “ERCOT has implemented EECP Step 1.” |
| 2 | ISSUE EECP Step 2: IF EECP Step 1 fails to maintain undeployed Responsive Reserve Service (RRS) above the largest unit in operation. |
| NOTE: | Normally the largest unit in operation will be STP 1 or 2 @ 1250 MW. |
| 2.a | - ISSUE a voice message to Transmission Operators “ERCOT has implemented EECP Step 2,” using the hotline, if available. - POST via ENS that “ERCOT implemented EECP Step 2.” |
| NOTE: | The Frequency Control Desk will issue a voice message, to all QSEs “ERCOT has implemented EECP Step 2. QSE are to notify ERCOT of any uncommitted units and their available time frame. QSEs are to report back to the ERCOT System Operator when requested step has been completed,” using the hotline if available. |
| 2.b | IF any unutilized capacity remain unavailable to the market issue VDI or OOM to use it. |
| 2.c | INSTRUCT Transmission Operators to reduce load by using distribution voltage reduction management tools, if deemed beneficial by the Transmission Operators. |
| 2.d | DEPLOY (remove from service) all Responsive Reserve, which is supplied from Loads Acting As a Resource (controlled by high-set under-frequency relays) to remove such load. |
| 2.e | IMPLEMENT Block Load Transfers (BLTs) by making a hotline call to all Transmission Operators and asking them to implement any available Block Load Transfers to remove load from ERCOT. |
| 3. | ISSUE EECP Step 3: IF Responsive Reserves continue to trend down, is no longer available, or IF frequency drops below 60 Hz, or begins to trend down, with no indication for recovery. |
| 3.a | - ISSUE a voice message to Transmission Operators “ERCOT has implemented EECP Step 3,” using the hotline, if available, - POST via ENS that “ERCOT implemented EECP Step 3.” |
| NOTE: | The Frequency Control Desk will issue a voice message, to all QSEs “ERCOT has implemented EECP Step 3. All QSEs confirm that their resources are at maximum output,” using the hotline if available. |
| 3.b | ERCOT will issue an appeal through the public media for voluntary load curtailment. See Shift Supervisor’s Procedure. |
| 4. | IMPLEMENT EECP Step 4: IF frequency falls below 59.8 Hz and above steps have not alleviated the event, or IF frequency falls below 59.5. |
| 4.a | - ISSUE a voice message to Transmission Operators “ERCOT has implemented EECP Step 4,” using the hotline, if available. - POST via ENS that “ERCOT implemented EECP Step 4.” |
| 4.b | In addition to measures listed above: - ERCOT will instruct, in 100 MW blocks, all TDSPs having control over distribution feeder breakers and/or control of breakers serving retail customer to shed load in order to maintain a steady state system frequency of 59.8 Hz. Block amounts are shown in the ERCOT Operating Guides. Typical Script: “ERCOT is instructing all Transmission Operators to shed their share of <amount> MWs. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load shed.” |
| 4c. | Inform the Frequency Control Desk Operator that notifications have been completed to the Transmission Operators to shed firm load. Instruct the Frequency Control Desk Operator to issue a voice message, to all QSEs “ERCOT has implemented EECP Step 4, <MW Amount> of firm load has been shed.” using the hotline if available. |

| ### 2.5.7 Restore EECP Steps |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | In the absence of the Shift Supervisor, the Frequency Control Desk will implement applicable steps of the EECP. |
| NOTE: | Numbering of procedure steps is reversed to coincide with EECP Steps. |
| 4. | Step 4 to Step 3 |
| 4.a | ENSURE frequency does not deviate significantly from 60.0 Hz and available Responsive Reserve Service is equal to largest unit on line. INSTRUCT TDSP Transmission Operator to maintain nominal voltage, using distribution voltage management tools deemed beneficial by the TDSP. INSTRUCT the Transmission Operators to restore the load, which was shed under EECP 4. Typical Script: “This is the ERCOT System Operator. ERCOT is instructing all Transmission Operators to now restore their share of <amount> MWs leaving <amount> MWs still off.” |
| NOTE: | ALL firm load must be restored before moving from EECP Step 4 to EECP Step 3. |
| 4.b | IF frequency does not deviate significantly from 60.0 Hz and available Responsive Reserve Service is equal to largest unit on line, and available firm load shed under EECP Step 4 has been restored, then move from Step 4 to 3. |
| 4.c | - ISSUE a voice message to Transmission Operators “ERCOT is moving from EECP Step 4 to 3,” using the hotline if available. - POST via ENS that “ERCOT reduced EECP Step 4 to 3.” |
| 4.d | Instruct the Frequency Desk to issue a voice message, to all QSEs “ERCOT is Moving from EECP Step 4 to 3,” using the hotline, if available. |
| 3. | Step 3 to Step 2 |
| 3.a | ERCOT will rescind through the public media, voluntary load curtailment. |
| 3.b | WHEN it appears that voluntarily curtailed load has been restored to a reasonable extent, AND: - Frequency does not deviate significantly from 60.0 Hz - Undeployed Responsive Reserve has been restored to a level at least equal to the largest unit in service |
| 3.c | - ISSUE a voice message to Transmission Operators “ERCOT is moving from EECP Step 3 to 2,” using the hotline, if available. - POST via ENS that “ERCOT reduced EECP Step 3 to 2.” |
| 3.d | Instruct the Frequency Control Desk to issue a voice message, to all QSEs “ERCOT is moving from EECP Step 3 to 2,” using the hotline, if available. |
| 2. | Step 2 to Step 1 |
| 2.a | ENSURE frequency does not deviate significantly from 60.0 Hz and undeployed Responsive Reserves are sustainable at the largest unit operating on line to proceed. |
| 2.b | RESTORE (return to service) Loads Acting As a Resource (controlled by high-set under-frequency relays), as available. ENSURE under-frequency relays are reset. |
| 2.c | ISSUE Verbal Dispatch Instructions (VDI) as necessary to allow OOMd units to return to reserve status, managing congestion where required. |
| 2.d | IF frequency does not deviate significantly from 60.0 Hz and scheduled Responsive Reserve is restored to 2300 MW THEN move from Step 2 to Step 1. - ISSUE a voice message to Transmission Operators “ERCOT is moving from EECP Step 2 to 1,” using the hotline, if available. - POST via ENS that “ERCOT reduced EECP Step 2 to 1.” |
| 2.e | Instruct the Frequency Control Desk to issue a voice message, to all QSEs “ERCOT is moving from EECP Step 2 to 1,” using the hotline, if available. |
| 1 | Step 1 to Termination |
| 1.a | ENSURE that the following has been accomplished: - Recall NSRS that was deployed. - CONTACT AEP and cancel Emergency Assistance procurement |
| 1.b | IF ERCOT frequency does not deviate significantly from 60.0 Hz AND undeployed Responsive Reserve Service is 2300 MW THEN TERMINATE EECP. - ISSUE a voice message to Transmission Operators “ERCOT is terminating EECP,” using the hotline, if available. - POST via ENS that “ERCOT is terminating EECP.” |
| 1.c | Instruct the Frequency Control Desk to issue a voice message, to all QSEs “ERCOT is terminating EECP,” using the hotline, if available. |
| 1.d | ENSURE Southwest Power Pool Security Coordinator has been notified that “ERCOT is terminating EECP.” |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.