- ERCOT Operations Bulletin 285

ERCOT has revised the Transmission & Security Desk Procedure.  Revision includes updating section 2.4.4 – step 1.

| ### 2.4.4 VSAT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | To monitor system voltages and to prevent voltage collapse. |
| NOTE: | VSAT should be checked at least every hour, or more frequently as necessary. |
| NOTE: | To contact VSAT support, check the board in the back of TCC for the on-call personnel. |
| 1 | Determine if VSAT has run in the last 80 minutes. Reference Display: Network Online Sequence - If VSAT has not run in the last 80 minutes, contact VSAT support. - IF a South-Houston or North-Houston CSC/CRE has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. Otherwise, continue with following steps. - If any of the monitored VSAT scenario results approaches the safety margin listed in the table below, it is suggested to manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) more frequently than the periodic scheduled VSAT run and proceed to step 2. Otherwise, continue with the following steps. Safety Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 175MW. O-DFW_L; 175MW. S-H_G; 175MW. S-H_L; 175MW. N-H_G; 175MW. N-H_L; 175MW. O-VALL_L; 75MW. |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.