- ERCOT Operations Bulletin 298

ERCOT has revised the Frequency Control Desk Procedure.  Revision includes updating section 2.6.9 and 2.6.10.

| ### Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | IF Adjusted Responsive Reserve is equal to or less than 3000MW, issue an Advisory. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 2 | IF Adjusted Responsive Reserve is equal to or less than 2500MW, issue an Alert. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 3 | Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. |
| 3a | Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. |
| 3b | Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive reserves. |

| ### Diminishing Reserve Notice Cancellation Guidelines |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
| 1 | Cancel an Alert or Advisory if: - ARR is >= 3200 MWs, AND - Load is trending down, OR - The MAI shows the “Max Cap Room” increasing over the next two hours |
| 2 | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
| 3 | IF an alert has been canceled, - NOTIFY QSEs that all RMRs may return to normal operation, AND - Performance testing may be resumed. Typical Scripts: Cancel Advisory - “This is the ERCOT System Operator. ERCOT is canceling the Advisory for notice of Adjusted Responsive Reserve. Adjusted Responsive Reserves are now <amount>MWs.” Cancel Alert - “This is the ERCOT System Operator ERCOT is canceling the Alert for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now <amount>MWs. At this time, all RMRs should continue normal operation. Performance testing may resume.” |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.