- ERCOT Operations Bulletin 301

ERCOT has revised the Transmission & Security Desk.  Revision includes updating sections 2.5.6 and 2.5.7.  All steps have been revised and rewritten.

| 2.5.6 Implement EECP |  |
| --- | --- |
| Step # | Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 3. |
| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MWs, OR - ERCOT has deployed over 760MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| 1b | Using the hotline, notify all TOs to implement EECP STEP 1. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT has implemented EECP STEP 1.” |
| 1c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |
| 1d | Ensure the following is complete: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 2a | In addition to measures associated with STEP 1; Implement EECP Step 2 IF, - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| 2b | In conjunction with the ERCOT Frequency Control Desk Operator, implement EECP STEP 2. Using the hotline, notify all TOs to implement EECP STEP 2. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor Typical script: “ERCOT has implemented EECP STEP 2; - LaaRs have been deployed - Within the time frame of the emergency, TOs that have the ability are to implement Block Load Transfers and transfer load from the ERCOT control area to Non-ERCOT control areas - If local operating conditions permit, TOs are to reduce customer loads by using distribution voltage reduction measures - Report back to ERCOT when these actions have been initiated and/or completed |
| 2c | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures that have been taken. |
| 2d | Unless a media appeal is already in effect, issue an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) |
| 3a | In addition to measures associated with STEP 1 & 2; Implement EECP Step 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| NOTE: | Firm load is to be shed in 100 MW blocks. TOs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of EECP. |
| 3b | Using the hotline, notify all TOs to implement EECP STEP 3. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT has implemented EECP Step 3. ERCOT is instructing all Transmission Operators to shed their share of <amount> MWs. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load shed.” |
| 3c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |
| 3d | Inform the Frequency Control Desk Operator that notifications have been completed to the Transmission Operators to shed firm load. |
| 3e | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures have been taken where possible - Load shed instructions have been received and enacted. |

| 2.5.7 Restore EECP Steps |  |
| --- | --- |
| Step # | Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP Restoration. Numbering of procedure steps is reversed to coincide with EECP Steps. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| 3 | Begin restoring firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MWs |
| 3a | Using the hotline, notify all TOs of firm load restoration. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical Script: “ERCOT is instructing all Transmission Operators to now restore their share of <amount> MWs leaving <amount> MWs still off. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load restored.” |
| 3b | Ensure the following: - “ERCOT is restoring firm load” is posted on the Emergency Notification System (ENS) short version – 32 characters - “ERCOT is restoring firm load” is posted on the Market Information System (MIS) |
| 3c | Maintain Adjusted Responsive Reserve supplied from generation equal to 1150 MWs while restoring firm load. |
| 3d | Ensure that the Frequency Control Desk Operator notifies the QSEs that firm load is being restored. |
| 3e | Move from EECP STEP 3 to STEP 2 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored |
| 3f | Using the hotline, notify all TOs of the reduction from EECP Step 3 to Step 2: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT is moving from EECP Step 3 to Step 2.” |
| 3g | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |
| 3h | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |
| 3i | When directed by the Frequency Control Desk Operator, use the hotline and notify the TOs that LaaRs are being restored. |
| 3j | Resend distribution voltage reductions measures as appropriate. |
| 2 | Move from EECP STEP 2 to STEP 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - LaaRs are fully restored, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 2a | Using the hotline, notify all TOs of the reduction from EECP Step 2 to Step 1: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT is moving from EECP Step 2 to Step 1.” |
| 2b | Ensure the following: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 to Step 1 is posted on the Market Information System (MIS) |
| 2c | If Block Load Transfers have been executed, restore them as system conditions permit. Typical Script: “TOs who have transferred load to Non-ERCOT control areas may restore such load as local conditions permit. Keep ERCOT advised on the progress and completion this task” |
| 2d | Instruct the Frequency Control Desk to notify QSEs that BLTs are being restored. |
| 2e | Appeal through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisors procedures) |
| 2f | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |
| 1a | Move from EECP Step 1 to Termination when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MWs, AND - All uncommitted units secured in EECP STEP 1 can be release to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 1b | Using the hotline, notify all TOs of the reduction from EECP Step 1 to termination: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT is terminating EECP. An Alert still remains in effect.” |
| 1c | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.