- ERCOT Operations Bulletin 308

ERCOT has revised the Day Ahead Desk.  Changes include updating the methodology for determining non-spin procurement.  Highlighted portions indicate sections that were updated.

Appendix 4:  Methodology for Determining Non-Spin Procurement

Use the following in determining the amount of NSRS needed:

- IF the current month is April, May or October, then purchase NSRS in amounts equal to the largest unit online for the hours projected within 85% of peak hour.

- For other months of the year,

- IF today’s and tomorrow’s ERCOT high temperature is projected above 95 degrees in Dallas/Ft. Worth or Houston, THEN PURCHASE NSRS in amounts equal to the largest unit online for the hours projected warmer than 95 degrees.

OR

- If tomorrow’s low temperature forecast is projected below 30 degrees in Dallas/Ft. Worth or Houston, THEN PURCHASE NSRS in amounts equal to the largest unit online for

  - the projected morning load pickup hours and

  - hours projected within 85% of peak hour.

OR

- Review the next day Resource Plans after the Day Ahead RPRS study or market is complete.  When the Resource Plan appears to have been updated, and an accurate determination of Non-Spin Reserves for the next day can be made, open a secondary NSRS market as needed for hours in which the Market Analyst Interface (MAI) indicates less than 3300 MW of spinning reserve.

Reference:

www.ercot.com  “ERCOT Methodologies for Determining Ancillary Service Requirements – Current”

A copy of the procedure is available at http://www.ercot.com/mktrules/guides/procedures/index.html.