ERCOT Operations Bulletin 320

ERCOT has revised the Frequency Control Desk section of the Operating Procedure Manual.

Changes include updating section 2.6.9 and 2.6.10

| ### Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | IF Adjusted Responsive Reserve is equal to or less than 3000MW, issue an Advisory. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” |
| 2 | IF Adjusted Responsive Reserve is equal to or less than 2500MW, issue an Alert. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” Implement the following actions: - Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. - Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. - Deploy Non-Spin and “Quick Start” GTs as follows: - If Non-Spin is available, deploy a minimum of 500 MWs. Deplete this resource before proceeding to b. - If Non-Spin is unavailable or if all Non-Spin has been utilized, dispatch to full output, as many “Quick Start” GTs as necessary, bid into the Balancing Market that show “On” and “Plan MW” 0 to recover ARR. Deplete these resources before proceeding to c. - If all “Quick Start” GTs that were “On” are depleted, OOMC/OOME the remainder of the “Available” “Quick Start” units to recover ARR. Deplete these resources before proceeding to d. - If all “Quick Start” units are depleted, OOMC/OOME any additional “Available” units to recover ARR. |

| ### 2.6.10 Diminishing Reserve Notice Cancellation Guidelines |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
| 1 | Cancel an Alert or Advisory if: - ARR is >= 3200 MWs, AND - Load is trending down, OR - The MAI shows the “Max Cap Room” increasing over the next two hours |
| 2 | As system conditions permit, recall/release incrementally, any additional generation that was brought online to recover ARR. |
| 3 | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
| 4 | IF an alert has been canceled, - NOTIFY QSEs that all RMRs may return to normal operation, AND - Performance testing may be resumed. Typical Scripts: Cancel Advisory - “This is the ERCOT System Operator. ERCOT is canceling the Advisory for notice of Adjusted Responsive Reserve. Adjusted Responsive Reserves are now <amount>MWs.” Cancel Alert - “This is the ERCOT System Operator ERCOT is canceling the Alert for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now <amount>MWs. At this time, all RMRs should continue normal operation. Performance testing may resume.” |

A copy of the procedure is available at

http://www.ercot.com/mktrules/guides/procedures/index.html