ERCOT Power Operations Bulletin #348

ERCOT has revised the Shift Supervisor Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure is available at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### 2.2.10 TRE Investigation Reporting |  |
| --- | --- |
|  | ###### Procedural Steps |
| NOTE: | There are certain events listed in the Event Investigation Process that requires an e-mail from System Operations to ERCOT Operations Support and the TRE. An initial report from System Operations will trigger the investigation process. The subject line of the e-mail should read “TRE Investigation Reporting.” |
| NOTE: | Events that are deemed to be significant include, but are not limited to, the following: - EECP Implementation - Emergency Notice issued - Simultaneous loss of any combination of three generating unit facilities, transmission lines, and autotransformers (138KV and above). Note: Count combined cycle trains as one unit - SPS activation - RAP implementation requiring load shedding - Under frequency relay operations (or frequency deviations greater than .3Hz from scheduled frequency) - Sustained voltage deviations greater than five percent on 345 Kv systems - Alerts for significant transmission elements (345 Kv) - Failure of computer systems at ERCOT, the Qualified Scheduling Entity (QSE) or Transmission Operator (TO) - Voltage collapse on portions of 138 Kv or 345 Kv system - Loss of an ERCOT, QSE, or TO control center - Black Start initiation - Uncontrollable loss of 150 MW or more of firm load shed for more than 15-minutes from a single incident |
| NOTE: | There are also DOE and several NERC reportable events that could trigger an investigation. To report such an event, see section 2.2.11. |
| 1 | When a significant event occurs, within one hour complete the form located in Attachment B “Event Investigation Form” and e-mail to distribution group entitled “TRE Investigation Reporting.” |

| ### 2.2.11 NERC and DOE Disturbance Reporting |  |
| --- | --- |
|  | ###### Procedural Steps |
|  | When Disturbance reporting is required: |
| NOTE: | NERC E-mail address: esisac@nerc.com, fax (609) 452-9550 DOE E-mail address: doehqeoc@oem.doe.gov, fax (202) 586-8485 DOE Operation Center voice phone: (202) 586-8100 ERCOT Compliance E-mail address: 1 ERCOT Compliance Team Send e-mail to distribution list entitled “NERC and DOE Disturbance Reporting.” |
| NOTE: | NERC Standard EOP-004-1 R3.1 requires a copy of the NERC Interconnected Reliability Operating Limit and Preliminary Disturbance Report to be submitted by the affected Operating Authority within 24 hours of the disturbance or unusual occurrence. |
| 1 | Forward the TDSP(s) report or the Director of Cyber Security’s report to ERCOT Compliance, NERC, and DOE. Ensure all three entities receive a report. (e.g. If TDSP or Director, Cyber Security sends a report to only one entity; make sure the other two entities receive a report as well.) |
| 2 | If ERCOT is required to issue a report to NERC and DOE even when the disturbance does not require a report from a TDSP (e.g. The disturbance involves two or more TDSPs area to meet the requirements for reporting.) of if a report is received from the Director, Cyber Security, then do the following: - Complete required reports per NERC Attachment 1-EOP-004. - Complete required reports per DOE OE-417. - Forward reports to ERCOT Compliance, NERC, and DOE. |
| NOTE: | NERC Attachment 1-EOP-004 to report a disturbance can be downloaded at ftp://www.nerc.com/pub/sys/all_updl/oc/dawgstandards/rs//NERC_EOP-004-1_Form NERC IROL and Preliminary disturbance Report.doc DOE Form OE-417 to report a disturbance or cyber attack can be downloaded at http://www.eia.doe.gov/oss/forms.html. |

| ### 2.2.12 PUC Daily Report |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The PUC reports are to be generated twice per day: In winter months at 0100 and 0500 In summer months at 1100 and 1500 The timing change will be determined by the Manager, System Operations. |
| NOTE: | Be able to provide a list of unplanned generation outages for the day if requested by the PUC. |
| 1 | Complete the PUCT Daily Report template at the appropriate times. E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Do not add editorial comments to this report that reveal market sensitive data. General comments that convey overall system conditions are allowed. |
|  | Revise the last report sent and resend it if: - The probability of an EECP event increases. Give reason(s) for escalation, OR - Conditions change that required new notices to be issued or cancelled, such as, an OCN , Advisory, Alert, or Emergency Notice OR - A shortage of generation capacity develops OR - Local reliability concerns arise which include actual overloads and/or loss of load, especially the Laredo area, OR - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if there are unplanned outages of the generation units in the area. - “ERCOT only” NERC and/or DOE event occurs. These events are market sensitive so provide a brief description without the market sensitive information. - DCS event occurs |
| 2 | Use the following guidelines to determine the potential for EECP when completing the PUCT Daily Report: Potential for EECP 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves. - Medium - An Alert is in effect for Adjusted Responsive Reserves. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - High - An Alert is in effect for Adjusted Responsive Reserves and trending downward after procuring quick-start capacity. - Critical - EECP Step 1 in effect |
|  | Potential for EECP 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves - Medium - EECP Step 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EECP Step 2 in effect |
| 3 | Potential for EECP 3 - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EECP Step 2 in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EECP Step 3 in effect |
| 4 | Potential for EECP 4 - Low - Sufficient capacity to cover peak demand - Medium - EECP Step 2 in effect - High - EECP Step 3 in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EECP Step 4 in effect |

3.3 Appendix 3  ERCOT EECP and NERC EEA Notifications Requirements

| Condition | Notified Entity | Notification Type | Time | How Notified | Update Requirements |
| --- | --- | --- | --- | --- | --- |
| EEA 1 | NERC | RCIS | ASAP | Via web link | As changes occur, minimum of 1 hour. |
| EECP 1 EEA 1 | TRE, NERC & DOE | Event Investigation Form RCIS | ≤ 1 Hour ASAP | E-mail Via web link | As changes occur, minimum of 1 hour. |
| EECP 2, EEA 2 | TRE, NERC & DOE | Event Investigation Form RCIS EIA-417 - Schedule 1 EIA-417 – Schedule 2 | ≤ 1 Hour ASAP 1 Hour 48 Hours | E-mail Via web link DOE web link DOE web link | As changes occur, minimum of 1 hour. |
| EECP 3, EEA 2 | TRE, NERC & DOE | Event Investigation Form RCIS EIA-417 - Schedule 1 EIA-417 – Schedule 2 | ≤ 1 Hour ASAP 1 Hour 48 Hours | E-mail Via web link DOE web link DOE web link | As changes occur, minimum of 1 hour. |
| EECP 4, EEA 3 IROL | TRE, NERC & DOE NERC | Event Investigation Form RCIS EIA-417 - Schedule 1 EIA-417 – Schedule 2 NERC Prelim. Report Final Report NERC Prelim. Report | ≤ 1 Hour ASAP 1 Hour 48 Hours 24 Hours 60 Days 72 Hours | E-mail Via web link DOE web link DOE web link | As changes occur, minimum of 1 hour. |
| Alert 0 | NERC | RCIS | ASAP | Via web link | Upon termination of EEA |

NOTE:  RCIS - Reliability Coordinator Information System

EEA – Energy Emergency Alert

LINKS:

RCIS - https://scis.nerc.net/scis.asp

NERC - ftp://www.nerc.com/pub/sys/all_updl/oc/dawgstandards/rs//NERC_EOP-004-1_Form NERC IROL and Preliminary disturbance Report.doc

DOE - ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc

Event Investigation Form - Attachment B