ERCOT Power Operations Bulletin #350

ERCOT has revised the Frequency Control Desk Manual.

The specific changes are shown below

A copy of the procedure is available at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### Review AGC Performance |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| GOAL: | Maintain CPS1 over 100. Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Ancillary Service Performance Monitor – Regulation Services |
| 1 | If performance drops below 100 for over three consecutive hours, attempt to identify the reason. Actions that may be taken are: - Check Regulation Service to be available during the time frame. - If Regulation Service was depleted check with Operating Period Desk and inquire if enough Balancing Energy has been deployed to restore Regulation Service. - If Regulation Service was depleted check for QSEs with large SCE in the direction of the depleted Regulation Service. If the cause for the large SCE is unknown contact the QSE and inquire about the status of their SCE. |
| 2 | LOG in the Operator’s Log the event and the probable cause of the poor performance. |

## 2.5          Frequency Control

| ### 2.5.1 Frequency Control Operating Procedure |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| 1 | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or - “Last AGC Cycle” time on Generation Area Status display is not updating Place a large QSE (that has regulation reserve) on constant frequency. When frequency control is functioning, remove the QSE from constant frequency. |
| 2 | At the operator’s discretion, turn off SCE feedback for Regulation Providers with Participation Factors less than 1% (<0.01). |
| 3 | Monitor QSE generation and SCE: - Remove a QSE’s SCE feedback if they have a large SCE and their generation is not moving in the proper direction or rate to correct their SCE. Reference Display Responsive, Regulation, and SCE Regulation |
| 4 | NEVER (unless directed by the Control Engineer or designee): - Modify “Total (SCE-responsive) Feedback Gain” (should be altered by the Control Engineer) - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) Reference Displays: Responsive, Regulation, and SCE – Details |
| 5 | LOG in the Operator’s Log frequency deviations of greater than or equal to 0.10 Hz. Record the following: - Possible reasons if known. (SCE, Large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped. - Approximate MWs that was on the unit when the unit tripped. - Approximate ERCOT load. |

| ### 2.5.4 Operator Instructions for High Frequency |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
|  | The following steps are to be taken in the event of High system frequency of unknown cause. If the cause of High system frequency is known and system response or other actions are expected to correct it, then the following steps are optional. |
| NOTE: | The Frequency Control Desk Operator may consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. |
|  | Frequency above 60.05 and continuing to climb or over 60.05 > five minutes. |
| 1 | If regulation down service remains and is deploying: - Call QSE’s with positive SCE and direct them to reduce generation to return their SCE to zero as soon as possible. - Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
| NOTE: | Typically a 100 MW dispatch instruction during the winter months would be expected to have a 0.5 Hz influence, while during the summer months this would require ~200 MW of reduction. |
|  | Frequency above 60.10 and continuing to climb |
| 2 | If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE within five (5) minutes or no QSE appears to be hanging out: OR If no physical regulation down service is available: Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain 0 SCE) to reduce generation. Typical script: This is [operator’s first and last name] at ERCOT. VDI #_________ issued to [selected QSE]. Reduce your generation by <MW amount> due to a High Frequency Excursion. |
| 3 | Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
| 4 | Log the actions that were taken. |

## Outages

| ### 2.8.1 Maintenance Level 2 & 3 Outages |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTES: | Maintenance Level 2 and 3 outages are coordinated with the ERCOT Outage Coordination Group. These outages should not be “accepted” by anyone other than that group. However, until they are accepted in the Outage Scheduler, they will continue to show up every time the Outage Scheduler refreshes (that is about every two minutes). |
| 1 | DO NOT check the “accept” box for Maintenance Level 2 and 3 Outages in the Outage Scheduler. Instead, place those Maintenance Level 2 and 3 outages in “Study” status and notify the Outage Coordination group of the Maintenance Level 2 or 3 outage, by email to “OPS Outage Coordination”. |

## Appendix 4:  Telephone Hotline

NOTE: Ensure “Lost Souls” are cleared prior to making Hotline Calls.

| QSEs |  |
| --- | --- |
| AEN | Garland |
| AEP Ohio | IPAS |
| ANP | LCRA |
| APX Equinix | Merrill Lynch |
| BEPC (Brazos) | NRG |
| British Petro | Occidental Greenway |
| BTU | Reliant REPS |
| Calpine | Sempra |
| Constellation | STEC |
| Coral | SUEZ |
| CPSB | Tenaska |
| Direct Energy | Topaz |
| Eagle | TXU |
| ENCO (Energyco) | Weststar |
| Exelon | XTend |
| FP&L Juno Beach |  |
| FULCRUM |  |

| TOs |  |
| --- | --- |
| AEN | Garland |
| AEP | LCRA |
| BEPC | Magic Valley |
| BPUB | ONCOR |
| BTU | Rayburn |
| Centerpoint | STEC |
| College Station | TNMP |
| CPSB |  |
| Denton |  |