ERCOT Power Operations Bulletin #356

ERCOT has revised the Day Ahead Desk Procedure Manual.  effective December 31, 2007

The specific changes are shown below.

A copy of the procedure will be available after 12/31/2007 at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ## 2.3 Enter A/S Requirements & Review the System Conditions Forecast |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Step 1 must be completed prior to 0600. |
| 1 | Determine the amount of RRS obligation for hour ending 0700 through hour ending 2200 - Review the temperature forecast in these hours. - Set the Responsive Reserve obligation equal to 2300 MW for hours that are outside the hour ending 0700 through hour ending 2200 range. - Set the Responsive Reserve obligation equal to 2800 MW for hours between 0700 and 2200 in which the temperature forecast in either the North Central or Coast weather zone is equal to or greater than 95 degrees Fahrenheit. - Set the Responsive Reserve obligation equal to 2600 MW for hours between 0700 and 2200 in which the temperature forecast in either the North Central or Coast weather zone is equal to or greater than 85 degrees Fahrenheit but less than 95 degrees Fahrenheit. - Set the Responsive Reserve obligation equal to 2500 MW for hours between 0700 and 2200 in which the temperature forecast in both the North Central or Coast weather zone is less than 85 degrees Fahrenheit. PUBLISH the hourly ERCOT system total Ancillary Service requirements for each of the following, for each hour of the operating day: (Refer to Appendix 3 if desired) - DRS - URS - RRS - NSRS (See Appendix 4) |
| NOTE: | Step 2 may be completed after 0600. |
| 2 | VERIFY by spot-checking the following information posted to the ERCOT Market User Interface (the Texas Market Link) or the ERCOT Public Web for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - Texas Market Link; Market Activities Tab; Outage Scheduler; Outage Scheduler; OR https://mostml.ercot.com/outages_prp/default.cfm OR - www.ercot.com; Grid Information Tab; Approved Transmission Outages link OR http://mospublic.ercot.com/ercot/jsp/planned_trans_out.jsp - MOI: Daily Operations Plan; Outage Schedule tab - Weather assumptions used to provide the system conditions forecast. - www.ercot.com; Grid Information Tab; Weather; OR http://mospublic.ercot.com/ercot/jsp/tem_peaks.jsp - MOI: No information - The forecast of hourly loads by Congestion Management Zones and hourly ERCOT System loads - Market Information Tab; Load Data link; Midterm Load Forecast OR http://mospublic.ercot.com/ercot/jsp/midterm_load_forecast.jsp OR - Texas Market Link; Market Activities Tab; Market Information; View Midterm Load Forecast - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – DRS, Regulation Up – URS, Responsive Reserve – RRS, and Non-spinning Reserve – NSRS. - Texas Market Link; Market Activities Tab; Market Information; Ancillary Service Requests OR - Market Information Tab; Energy and Ancillary Services link; Ancillary Services Bid Requests link; OR http://mospublic.ercot.com/ercot/jsp/ancillary_service_requests.jsp |

| ## A/S Requirement Posting |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | - BY the 20th of each month, use the “Message Administration” function on the Texas Market Link to post the projected Ancillary Services requirements for the following month. (See Appendix 1) Determine the A/S requirements as follows: - USE a constant value of 2300 MW for Responsive Reserve for hours ending 2300 through 0600 - Include the following statement: “RRS requirements for hours ending 0700 through 2200 will be a minimum of 2300 MW, but may be greater as determined day-to-day.” - Obtain values for Up and Down Regulation and DBES from Operations Planning. - Anytime changes to the Ancillary Services requirements are received, inform the market prior to the effective date and time, or immediately, if necessary. |