Power Operations Bulletin # 357

ERCOT has revised the Frequency Control Desk Procedure.

The specific changes are shown below.

A copy of the procedure is available at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### 2.2.3 Monthly Testing of Satellite Phone System |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Purpose: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| Note: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 2 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Attachment B of the ERCOT Satellite Phone User Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 3 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 4 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form (SEE Appendix 11). An electronic copy of this form is located in P:\ SYSTEM OPERATIONS ”Satellite Bridge Testing forms” folder. |
| 5 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is complete. |
| 6 | Log the test date and results in the ERCOT Operations Log. |
| NOTE: | Email Cagle Lowe regarding any Satellite phone problems during the test. |

| ### Implement EECP |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |  |  |
| NOTE: |  | Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |  |  |
| NOTE: |  | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue if necessary until an acceptable repeat back is received. |  |  |
| NOTE: |  | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |  |  |
| 1a |  | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MWs, OR - ERCOT has deployed over 760MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |  |  |
| 1b |  | Using the hotline, notify all QSEs to implement EECP STEP 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 1, QSEs are to enact the following”: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - Start and load all available RMR units to full capacity within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. |  |  |
| 1c |  | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |  |  |
| 1d |  | Ensure the following: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |  |  |
| 1e |  | Ensure all available Non-Spin has been deployed. |  |  |
| 1f |  | Contact the ERCOT DC Tie Desk and request that they implement the Emergency Assistance Procedure.2.7.8 |  |  |
| 1g |  | Inform the Transmission & Security Desk to implement their procedures to start Emergency Assistance across the South DC Ties. |  |  |
| 1h |  | VERIFY and log the following as appropriate: - All RMR units are at, or being loaded to, full capacity - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources - Available DC Tie capacity not being used by the market has been applied to the system. (Generally, this will not affect export schedules out of the ERCOT Control Area.) |  |  |
| 2a |  | In addition to measures associated with STEP 1 Implement EECP Step 2 IF: - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |  |  |
| 2b |  | Using the hotline, notify all QSEs to implement EECP STEP 2. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP STEP 2; - QSEs are to deploy all Loads acting as a Resource (LAARs) bid to supply Responsive Reserves Service within ten (10) minutes. - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed,” |  |  |
| 2c |  | Instruct the Transmission & Security Desk Operator to inform the TO via the Hotline that LAARs have been deployed. |  |  |
| 2d |  | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |  |  |
| 2e |  | Ensure the following: - EECP Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 is posted on the Market Information System (MIS) |  |  |
| 2f |  | Notify Southwest Power Pool (SPP) Security Coordinator. Typical script: “This is [operator's first and last name],ERCOT is declaring NERC EEA Step 2.” |  |  |
| 2g |  | Unless a media appeal is already in effect, issue an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) |  |  |
| 2h |  | Dispatch any unutilized remaining capacity. |  |  |
| 2i |  | VERIFY and log the following as appropriate: - RMR units are at, or being loaded to full capacity. - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources. - Available DC Tie capacity not being used by the market has been applied to the system. - LAARs have been deployed. - SPP Security Coordinator has been updated on ERCOT’s status. |  |  |
| 3a |  | In addition to measures associated with STEP 1 & 2; imPLEMENT eecp sTEP 3 IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |  |  |
| NOTE: |  | There is two separate blocks of EILS: The first is called EILS Business Hours: Business hours are defined as HE 0900- HE 2000 on Business days Monday through Friday not to include Holidays. The second is called EILS Non-Business Hours: Non- Business Hours are classified as any hour not defined as Business Hours. When a deployment of EILS is implemented and the event is still in effect when one Time Period (either Business Hours or Non-Business Hours) ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. QSEs representing EILS Resources that are obligated in the new Time Period shall not deploy the newly obligated EILS Resources unless instructed to do so by ERCOT. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. When issuing a VDI for EILS specify Non- Business Hours or Business Hours in the Instruction Section of the VDI. |  |  |
| 3b |  | Using the hotline, notify all QSEs to implement EECP STEP 3. When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 3. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted (Non-Business Hours or Business Hours) EILS Resources at (time) until further notice. All QSEs confirm that their generation resources are at maximum output.” |  |  |
| NOTE: |  | EILS Resources have 10 min. to comply with this instruction. If conditions develop that require implementing EECP step 4, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. |  |  |
| 3c |  | During EECP step 3, and prior to conditions that would warrant implementing step 4, determine the following: - Has the timeline for Non-Business hour EILS to Business hour EILS (or vice versa) been crossed? - If yes, are additional EILS Resources available for the new time period? - If yes, is deployment of additional EILS Resources needed in the current system condition? - If yes, deploy the new time period EILS Resources first, with a VDI to the QSEs via a Hotline call, and then end the VDI for the previous time period. If no, continue: |  |  |
| 4a |  | In addition to measures associated with STEP 1 & 2,3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |  |  |
| 4b |  | Ensure that the Transmission & Security Desk Operator has completed notifications to the Transmission Operators to shed firm load before proceeding to Step 4c. |  |  |
| 4c |  | Using the hotline, notify all QSEs to implement EECP STEP 4. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 4. Transmission Operators have been instructed to shed <MW Amount> of firm load. All QSEs confirm that their generation resources are at maximum output.” |  |  |
| 4d |  | Ensure the printed Hotline log has date and time information and forward it to the Shift Supervisor. |  |  |
| NOTE: |  | ERCOT must post NERC EEA Step 3 on the NERC RCIS before SPP will initiate an emergency schedule across the DC ties without a NERC tag being submitted. |  |  |
| 4e |  | Inform the ERCOT DC Tie Desk to implement the Emergency Assistance Procedure 2.7.9. |  |  |
| 4f |  | In conjunction with the Transmission & Security Desk Operator, - Ensure EECP Step 4 is posted on the Emergency Notification System (ENS) short version – 32 characters - Ensure EECP Step 4 is posted on the Market Information System (MIS) |  |  |
| 4g |  | VERIFY the following: - All recourses are at full capacity - All RMR units are at full capacity - Available Non-Spin has been deployed in the period of the emergency. - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended. - Available DC Tie capacity not being used by the market has been applied to the system - SPP Security Coordinator has been updated on ERCOT’s status - All LAARs have been removed from service. |  |  |

| ### Restore EECP Steps |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |  |  |
| NOTE: |  | The Frequency Control Desk will implement applicable steps of the EECP Restoration. Numbering of procedure steps is reversed to coincide with EECP Steps. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |  |  |
| 4a |  | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. |  |  |
| 4b |  | Move from EECP STEP 4 to STEP 3 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND All firm load has been restored. |  |  |
| 4c |  | Using the hotline, notify all QSEs of the reduction from EECP Step 4 to Step 3: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is moving from EECP Step 4 to Step 3.” |  |  |
| 4d |  | Ensure the following: - EECP Step 4 to Step 3 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 4 to Step 3 is posted on the Market Information System (MIS) |  |  |
| 4e |  | Inform the ERCOT DC Tie Desk to implement the Emergency Assistance Termination Procedure 2.7.10. |  |  |
| 4f |  | Begin recalling LAARs as sufficient capacity from generation becomes available. Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LAARs are being restored. |  |  |
| 4g |  | Instruct the Transmission & Security Desk Operator to notify the TOs that LAARs are being restored. |  |  |
| 3a |  | Move from EECP STEP 3 to STEP 2 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LAARs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |  |  |
| 3b |  | Using the hotline, notify all QSEs of the reduction from EECP Step 3 to Step 2: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is moving from EECP Step 3 to Step 2.” |  |  |
| 3c |  | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |  |  |
| 3d |  | Appeals through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisor desk procedure) |  |  |
| 2a |  | Move from EECP Step 2 to Step 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MWs AND - All LAARs have been restored or replaced with generation. |  |  |
| 2b |  | Using the hotline, notify all QSEs of the reduction from EECP Step 2 to Step 1: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and lst name]. ERCOT is moving from EECP Step 2 to Step 1.” |  |  |
| 2c |  | Ensure the following steps are complete: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 to Step 1 is posted on the Market Information System (MIS) |  |  |
| 2d |  | Recall EILS. Maintain a minimum of 2300 MWs of Adjusted Responsive Reserve. |  |  |
| 2e |  | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS is being recalled. |  |  |
| 2f |  | Update Southwest Power Pool Security Coordinator of ERCOT’s status. Typical script: “This is [operator’s first and last name]. ERCOT is canceling NERC EEA Step 2. ERCOT is moving to NERC EEA Step 1.” |  |  |
| 1a |  | Move from EECP Step 1 to Termination when: - EILS resources have been recalled. AND - All uncommitted units secured in EECP STEP 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |  |  |
| 1b |  | Using the hotline, notify all QSEs of the reduction from EECP Step 1 to termination: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is terminating EECP. An Alert still remains in effect.” |  |  |
| 1c |  | Ensure the following: - EECP Step 1 termination is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 termination is posted on the Market Information System (MIS |  |  |
| 1d |  | Inform the ERCOT DC Tie Desk to implement Emergency Assistance Termination Procedure 2.7.11. |  |  |

| ### 2.7.1 Approve NERC Tags for East and North DC Ties |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Step # |  | ###### Procedural Steps |  |  |
| PURPOSE: |  | A NERC Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments. |  |  |
| NOTE: |  | AEP TO in Columbus, Ohio is the Tie Operator for the East and North DC Ties. The designation in WebTrans for the East tie is DC_E and the North tie is DC_N. |  |  |
| - NOTE: |  | Each time a new or updated NERC E-Tag is submitted, the WebTrans system will automatically validate the NERC E-Tag. WebTrans will display whether the NERC E-Tag has passed or failed validation. The criteria ERCOT uses to validate NERC E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the NERC E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated NERC E-Tag. Currently the only validation criterion set to automatically deny a NERC E-Tag is “QSE Contract”. If this validation fails the NERC E-Tag will be automatically denied. WebTrans Reference Display: Tag Criteria Summary |  |  |
| 1 |  | When a new or updated tag is received in the OATI WebTrans system: 1.1 Determine if the following information is correct on the NERC E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - “ERCOT-E” or “ERCOT-N” is selected for the correct Point-of-Receipt (POR) or Point of Delivery (POD) portion of the physical path. - “CSWS” is included as a Scheduling Entity on the SWPP TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. If any of this information is incorrect on the NERC E-Tag, deny the tag, otherwise go to Step 1.2. 1.2 Determine if the tag passed or failed validation. - If the tag passes validation, go to Step 2.. - If the tag fails validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag fails validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |  |  |
| CAUTION: |  | Do not approve a NERC tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the tag approval timeline, the tag will automatically be passively denied. |  |  |
| 2 |  | Periodically refresh the QSE Summary display during the tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the tag data to the schedule: - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the NERC E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E-Tag. - If the tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |  |  |

| ### 2.7.2 Adjustment of DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | When an adjustment alarm is received in WebTrans: - Determine if the tag passed or failed validation. - If the tag adjustment passed validation , approve the adjustment. - If the tag adjustment failed validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag adjustment failed validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor |
| 2: | Periodically refresh the QSE Summary display during the tag adjustment approval window to determine if a QSE has changed an MOI schedule that is now making the NERC E-Tag fail validation. - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the NERC E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E- Tag. - If the tag equals the MOI schedule, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |

| ### 2.7.3 Curtailment of DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | When a curtailment alarm is received in WebTrans, - Approve the tag curtailment. Webtrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| 2 | If a QSE or SPP requests a tag be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |

| ### 2.7.4 Over Scheduling DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | If one or more NERC E-Tags are submitted that will cause a DC Tie to be overscheduled, DO NOT approve the NERC E-Tag(s). |
| 2 | Contact SPP by telephone to ensure they also show that the pending NERC E-Tag(s) will cause the DC Tie to be overscheduled. Inform SPP that ERCOT will not approve the pending NERC E-Tags until appropriate curtailments have been implemented so that the DC Tie will not be overscheduled. |

| ### 2.7.5 Managing and Documenting Daily Inadvertent |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N, EGPS_DC, ROAD_DC, or LAR_VFT) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen be either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TDSP for the North and East DC Ties - Contact AEP Corpus Christi TDSP for the Eagle Pass and Rail Road DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is unknown (database load, loss of ICCP etc.), overwrite the actual value in the WebTrans system. ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator, and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. - If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5. | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - AEP Checkout-West@aep.com |

| ### Managing Inadvertent Across the North DC Tie Due To Deadband Limitations |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Due to limitations with the control system of the North DC-Tie, a deadband of about (+/-) 27 MW will be considered for normal operation. The deadband will be considered in place of shutting the DC-Tie down. |
| 1 | When no schedules are flowing across the North DC Tie OR if the net scheduled value is less than 27MW, ensure that the direction of flow is not causing more inadvertent. |
| 2. | Coordinate with the DC Tie Operator to reverse the flow across the North DC Tie when necessary. |

| ### Managing Inadvertent Payback |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Payback will only be scheduled when there is room on the DC Tie(s). Power schedules of market participants will supersede any inadvertent payback schedule. Payback schedules are implemented by the DC Tie Operator. They will bias the DC Tie(s) and create inadvertent in the opposite direction. This will reduce the inadvertent values. |
| NOTE: | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback schedule information from the Manager of System Operations. |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TDSP for the North and East DC Ties - Contact AEP Corpus Christi TDSP for the Eagle Pass and Rail Road DC Ties, and the Laredo VFT. |
| 1 | Prior to the start of the Payback Schedule, call the DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback schedule. |
| 2 | Periodically check the WebTrans system to ensure that the inadvertent values are decreasing. If they are not decreasing or are increasing, call the DC Tie Operator to determine the reason. WebTrans Reference Display: Daily Inadvertent |
| 3 | Prior to the Payback Schedule stopping, call the DC Tie Operator and confirm the agreed upon stop time. |

| ### Emergency Assistance across the East and North DC Ties for EECP Step 1 |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | At times other Southwest Power Pool (SSP) desk operators will answer the telephone. You may need to ask for the Reliability Coordinator. |
| 1 | Notify the SPP Reliability Coordinator that ERCOT will be requesting emergency assistance. Determine what DC tie capacity is available for Emergency Assistance into ERCOT and confirm with SPP. Typical Script: “This is [operator’s first and last name]. At XX:XX, ERCOT declared NERC EEA 1. We will be contacting an ERCOT QSE to inquire about the availability of an EEA 1 schedule.” |
| 2 | If capacity is available, call the appropriate QSE and inquire if they can generate an EEA 1 schedule from their resources outside of ERCOT and bring the power across the DC ties into the ERCOT Control Area. - Ensure the appropriate QSE understands that they must obtain transmission service and create and submit a NERC E-Tag for the EEA 1 schedule to flow. - A VDI must be issued to the appropriate QSE for the EEA 1 schedule. |
| 3 | Notify the DC Tie Operator that an EEA 1 schedule will be flowing across the DC Tie(s). Typical Script: “This is [operator’s first and last name]. At XX:XX, ERCOT declared NERC EEA 1. An ERCOT QSE will be submitting a NERC E-Tag for an EEA 1schedule into ERCOT across the DC Tie(s). |

| ### Emergency Assistance across the East and North DC Ties for EECP Step 4 |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | At times other Southwest Power Pool (SSP) desk operators will answer the telephone. You may need to ask for the Reliability Coordinator. |
| 1 | Notify the SPP Reliability Coordinator: Typical Script: “This is [operator’s first and last name]. ERCOT is declaring NERC EEA 3. ERCOT is requesting SPP to immediately start an EEA 3 schedule into the ERCOT Control Area for any remaining DC Tie capacity.” |
| 2 | Inform the DC Tie Operator that SPP is starting an EEA 3 schedule into the ERCOT Control Area and that a NERC E-Tag will be created as soon as practicable. |
| 3 | When possible: - Contact the appropriate QSE and instruct them to create and submit a NERC E-Tag for the EEA 3 schedule. - Issue a VDI to the appropriate QSE for the EEA 3 schedule. |

| ### Emergency Assistance across the East and North DC Ties Termination of EECP Step 4 |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | At times other Southwest Power Pool (SSP) desk operators will answer the telephone. You may need to ask for the Reliability Coordinator. |
| 1 | Update Southwest Power Pool Security Coordinator of ERCOT’s status. Typical script: “This is [operator’s first and last name]. ERCOT is canceling NERC EEA Step 3. ERCOT is moving to EEA 2. |
| 2 | Coordinate the termination of any EEA 3 schedules coming across the DC Ties with SPP, The DC Tie Operator, and the appropriate QSE. |

| ### Emergency Assistance across the East and North DC Ties Termination of EECP Step 1 |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | At times other Southwest Power Pool (SSP) desk operators will answer the telephone. You may need to ask for the Reliability Coordinator. |
| 1 | Update the Southwest Power Pool Security Coordinator of ERCOT’s status: Typical Script: “This is [operator’s first and last name}. ERCOT is canceling EEA 1. ERCOT is moving to NERC EEA 0 (zero). |
| 2 | Coordinate the termination of any EEA 1 schedules coming across the DC ties with the DC Tie Operator and the appropriate QSE. |

| ### 2.7.12 Fast Start Emergency Schedules to Southwest Power Pool (SPP) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Every effort should be made to render assistance during emergency conditions. The Emergency schedule can start at anytime and is not required to be in the ERCOT MOI. A schedule should be put in the MOI as soon as allowable before the Operating Period Lockout. SPP will notify ERCOT that emergency assistance is needed. |
| 1 | VERIFY that providing emergency assistance to SPP will not put ERCOT in an insecure state, or worsen an existing insecure state. |
| NOTE: | SPP will contact the DC Tie Operator and arrange to maximize the DC tie output into SPP. It is not necessary to confirm that an emergency condition has been posted in the RCIS. SPP may need to act before the RCIS is updated. |
| 2 | Direct the Operating Period Desk to adjust the Offset to minimize the use of Regulation until the schedule is in the MOI. |
| 3 | When possible: - Contact the appropriate QSE and instruct them to create and submit a NERC tag for the emergency schedule (this can be done after-the-fact). - Issue a VDI to the appropriate QSE for the emergency schedule. |