Power Operations Bulletin #  362

ERCOT has revised the Transmission and Security Desk Procedure Manual

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

\

## 1.1	Purpose

This procedure provides the System Operator assigned to the Transmission and Security Desk with detailed procedures required for performing duties assigned to that position.

The Transmission and Security Desk shall ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outage will not occur as a result of the most severe single Contingency.  The Transmission and Security Desk directs Transmission Operators or other Market Participants as required while maintaining or restoring the security/reliability of the ERCOT System.

| ### 2.1.1 System Overview |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | REVIEW each of the following as necessary to confirm system reliability status - Alarms - Real Time Contingency Analysis (RTCA) - Approved and Forced Outages - Load Forecast - Daily Transmission Limits - Voltage and Stability Limits |

| ### 2.1.2 RTCA Constraint Validation |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 20 minutes. |
| 3 | If RTCA has not run within 20 minutes, refer to “RTCA Call Out Procedure” in section 2.1.3. |
| 4 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist, - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are located in the daily Outage Notes. |
| 4a | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or - 4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take the DIRECT appropriate voltage control action. |
| 5 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 6 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Addendum 1 for guidance. |
| 7 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 8 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 9 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 10 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Take additional manual actions as necessary to resolve the contingency overload within 30 minutes. As time permits, notify the on-call Operations Support Engineer. If the system operator determines that the Pre-contingency value or system topology is incorrect, OR if a SPS, RAP, PCAP, TOAP, or MP exists, step 10 may be omitted. |
| 11 | If congestion management techniques fail to resolve congestion and the transmission system is beyond first contingency criteria, ISSUE an Alert per section 2.5.3. |
| 12 | Periodically check the Base Case violations display for Thermal overloads. |
| 13 | If a Thermal overload exists in real time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, OR if a SPS, RAP, PCAP, TOAP, or MP exists, step 13 may be omitted. |
| 14 | Periodically check the “Contingency Solution Results” display. If there are more than five (5) unsolved contingencies, run the State Estimator again. If more than five (5) remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. - Contingencies that are known to remain unsolved, or have been reported before, should not be included in the five (5) mentioned unsolved contingencies. |

| ### 2.1.3 RTCA Call Out Procedure |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The groups named below are distinct and serve different functions in this procedure. - Operations Planning Engineer - Operations Support Engineer - State Estimator Support Engineer The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions, required to ensure system security. |
| 1 | During normal business hours, if RTCA has not solved within the last 20 minutes, examine the branch violations by clicking the Branch button in the “Alarm and Violation” section on the left-hand side of the screen. If no unreasonable violations exist, then examine the contingency violations by selecting “Show Violations” in the section under Contingency Analysis at the bottom of the screen. If, after trying all the checks RTCA still has not solved, ask the Shift Supervisor to notify the on-call State Estimator Support Engineer and request that RTCA be restored to operation as soon as possible. |
| 2 | If RTCA has NOT solved within the last four hours, OR if the State Estimator Support Engineer informs the system operator that RTCA cannot be repaired within a reasonable amount of time, NOTIFY the on-call Operations Support Engineer. REQUEST local limits to use in place of RTCA, UNLESS a set of backup limits have been previously provided. |
| 3 | During after hour and weekend/holiday operations, IF RTCA has not solved within the last 20 minutes, INVESTIGATE why by using the list of State Estimator Checks outlined in Appendix 8. |
| 4 | If, after trying all the checks RTCA still has not solved, NOTIFY the on-call State Estimator Support Engineer and request that RTCA be restored to operation as soon as possible. |
| 5 | If RTCA has not solved within the last four hours, OR if the State Estimator Support Engineer informs the system operator that RTCA cannot be repaired within a reasonable amount of time: CALL the on-call Operations Support Engineer and REQUEST local limits to use in place of RTCA, UNLESS a set of backup limits have been previously provided. |

| ### 2.1.4 OOME – VDI Guidelines |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 1 does not apply to wind units. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOMEd off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, issue a VDI to relieve the QSE from their Ancillary obligation. Should system conditions warrant, a second market may be necessary to procure additional Ancillary Services. Inform the Shift Supervisor that it may be necessary to open a second market. |
| 5 | When a TO informs ERCOT of an SPS activation and the SPS activation de-rates a resource or takes a resource off line, issue a VDI to the affected QSE. - Record the generation level immediately after the duration. - Only list the beginning of the interval, the ending interval is not necessary. - If the resource is a DC tie, include the name and zone of the tie. - Record the time the SPS was cleared. |
| 6 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with an OOMC VDI for settlements. |
| 7 | As time permits, forward the VDI to the Shift Supervisor. |

| ### 2.1.5 Monitoring Outages |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Mark the required outages in the Outage Scheduler Real-Time Monitor. |
| 2 | Verify that the outage is being monitored by change in color to red. |
| 3 | Monitor outages as required. |

| ### 2.1.6 Alarm Processing and Acknowledgment |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: Page 1: 345 KV Transmission Equipment Status Page 2: 138 KV Transmission Equipment Status Page 3: Generator Breaker, AVR, and SPS Status Page 4: Transmission Line Overloads and Voltage Violations- critical alarms Page 5: AGC Status Page 6: RTNET Status Page 7: ICCP Status Page 8: EMS Task Application Status |
| 1 | Monitor the Alarm Summary Display pages 1, 2, 3, 4, and 8 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Frequency Control Desk to clear the alarms approximately every 2 to 3 hours or as needed. |

| ### 2.2.1 RTCAM Congestion Management |  |
| --- | --- |
| Step # | Procedural Steps |
| NOTE: | Local Congestion Management Techniques consist of OC3s, Unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| 1 | VERIFY SFT is enabled in the MOI. - This can be determined by making sure that the check box next to “Run SFT for Real-Time Markets” on the Real-Time Balancing Market display is checked. If it is not checked, then check it. |
| 2 | DETERMINE if RTNET and RTCA has solved within 20 minutes. |
| 3 | If RTNET and RTCA have not solved within 20 minutes, refer to the “RTCA Call Out Procedure” in Section 2.1.3 |
| 4 | DETERMINE if RTNET has solved with a solution status of “VALID SOLUTION – NO SFT CASE.” - If RTNET has this solution, notify the State Estimator On-Call Engineer. |
| 5 | If RTCA has solved within 20 minutes, EXAMINE the RTCAM Branch Violations and Operating Constraints List. |
| 6 | EXAMINE the constraints with the “Active” check box filled in. - VERIFY that an OC3 is created for all overloaded active constraints in the MOI by selecting the “constraint” tab from the “Real-Time Balancing Market” screen in the MOI. In the Type column, sort descending. All OC3s will be sorted to the top of the page. - If an overloaded constraint is active in RTCAM, but the corresponding OC3 is missing from the MOI, LOWER the value in the “% Rating” column in RTCAM to tighten the constraint until the OC3 appears in the MOI. - If an OC3 is active in the MOI, but the corresponding constraint in RTCAM is well below the monitored rating, INCREASE the value in the “% Rating” column in RTCAM to loosen the constraint. |
| 7 | To activate a constraint, check the “Active” check box next to the constraint to be activated. The text in this row of data will change to red and it will be immediately sorted to the top of the display. |
| 8 | To deactivate a constraint, uncheck the “Active” check box next to the constraint. Uncheck the “Retain” check box as well, if desired. Leaving the “Retain” box checked will only cause the constraint to remain on the Operating Constraints List display when an overload is not occurring. |
| 9 | To acknowledge constraints that are determined to be erroneous or are already accounted for, check the check box in the “Ack.” Column. This will sort the constraint to the bottom of the display. |
| 10 | Special Protection Schemes (SPS), Remedial Action Plans (RAP), and Pre-Contingency Action Plan (PCAP) analysis - EXAMINE the results in RTCAM for RAP or SPS activation, using the “SPS” and “RAP” columns on the Operating Constraints List display. - If “SPS” and/or “RAP” is checked, EXAMINE the color of the background. Refer to Appendix 4.1 for actions to be taken based on the color of the background. - ADJUST initial “% Rating” higher if activating a constraint for a post-RAP/SPS overload if needed. This is because RTCAM/SFT can not model RAP/SPS when generating OC3 constraints so they tend to over-constrain at 100 % of rating. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |

| ### 2.2.2 OOME when OC3 not Effective |  |
| --- | --- |
| Step # | Procedural Steps |
| NOTE: | All wind units have the non-bid flag checked in the Resource Plan which will prevent them from receiving local congestion instructions. When OC3 activation is not effective due to excessive wind generation output, the following steps shall be taken to OOME wind generation to relieve transmission congestion. |
| NOTE: | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Corrective action must be taken within 30 minutes to reduce the flow below 125%. |
| 1 | Activate an OC3 for local congestion as mentioned in Section 2.2.1. |
| 2 | Upon activation of the OC3, perform a Contingency Analysis study as indicated in Appendix 2 of this procedure. |
| 3 | After performing a Contingency Analysis study, navigate to the Network Constraints Summary by going to Analyst Displays  Contingency Analysis Displays  Shift Factors, or typing NETSENS_CONSTRAINTS in the command line at the top of the display. |
| 4 | On the Network Constraints Summary Display, scroll to the constraint for which the corresponding OC3 was created. Click on the circle with an “i” inside it on the right hand side of the display. This will bring up the Network Constraints Details. |
| 5 | The Network Constraints Details display shows all units which have positive or negative shift factors above 2 % for the given constraint. Scroll through this list to find the wind units with the greatest positive shift factors. Compare this list with the resource plan in the MOI. For wind units where the LSL and HSL are the same, OOME the units to 0 output, starting with the units with the highest positive shift factor as they can not respond to Down Balancing instructions. To determine how many units to OOME to zero, use the rule of thumb that the MW output of the units times their shift factor will be approximately the amount of MW change expected on the overloaded element of concern. |

| ### 2.2.3 Zonal (CSC) Congestion Management |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTES: | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severs single contingency. Potential IROLs are defined in the day-ahead analyses or when changes in system conditions warrant further evaluation. If a CSC has been marked as an IROL on the “Transmission Limits” sheet, ensure the limit is honored. If the limit is violated, take all possible actions to get below the limit in 30 minutes or less. The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary, to ensure system security. |
| 1 | When a CSC approaches or exceeds its limit on the “Transmission Limits to be Monitored” daily report, EMPLOY Zonal Techniques. - As the CSC approaches its limit, the system operator may use his/her discretion when to implement congestion management, either before or at the time the limit is exceeded, depending on system conditions. |
| 2 | When RTCA shows a post contingency overload on a CSC, AND the CSC has not exceeded its’ limit on the “Transmission Limits to be Monitored” daily report, AND RTCA has solved within the last 10 minutes, then RTCA results should be used as a basis for managing zonal congestion. |
| 3 | If Zonal Techniques fail to control the flow within NERC requirements, utilize Local Congestion Management Techniques. - Use the MIS to post that local techniques are being used to control CSC congestion. Typical Script: “Zonal congestion management techniques have been unsuccessful in controlling the “<zone – zone>” CSC. Local techniques will be utilized.” |
| 4 | If OOME becomes necessary, units that have their HSL and LSL set to the same value cannot respond to market deployments and may be deployed to 0 output. |
| 5 | IF RTCA values are being used to control a CSC due to a significant unexpected change in system conditions which is likely to last for an extended period of time, - NOTIFY Operations Support to determine if a new limit should be calculated. |
| 6 | IF a new Zonal limit is calculated by Operations Support, post it on the MIS and ENS, AND control to the new limit. |
| NOTE: | Zonal limits may change due to an outage cancellation, extension of an outage, or the early completion of an outage. |

| ### 2.2.4 West-North Dynamic Stability Limit |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | If the West-North limit calculated on the spreadsheet changes value or color, update the RTMONI limit on the “Stability-WN” monitor to the value shown on the spreadsheet. |
| 2 | If the monitored flow on the Stability-WN monitor exceeds the limit, activate the West – North OC1. Post a message on the MIS and ENS: Typical Script: “ERCOT is controlling the West to North Dynamic Stability Limit with the West – North OC1”. |
| 3 | If Zonal Techniques fail to control the flow within 15 minutes, utilize Local Congestion Management Techniques. Post a message on the MIS and ENS: Typical Script: “Zonal congestion management techniques have been unsuccessful in controlling the West to North dynamic stability limit. Local techniques will be utilized.” |
| 4 | Units that have their HSL and LSL set to the same value cannot respond to market deployments and may be deployed to 0 output |

| ### 2.2.5 OC1 Limits for Outage Support |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Adjust OC1 limits as required to support an outage. 1.1 If flow across a CSC is already below the limit required to support an outage, then it is permissible to wait and adjust the OC1 limit at the scheduled start time of the outage. 1.2 IF flow across a CSC is above the limit required to support an outage, then adjust the OC1 limits for intervals preceding the scheduled outage start time such that flow across the constraint is gradually reduced to at or below the limit required to support the specific outage. - While this action might result in over-constraining for a brief period, it is preferable to the negative effects of a sudden reduction in the OC1 limit. |
| NOTE: | If step 1.2 is required, use the MIS and post that ERCOT is controlling to a limit other than the one posted. Typical Script: The “CSC Name” limit will change to “MW Amount” at “Time”. ERCOT will start controlling to this limit in accordance with Section 2.2.3 of the Transmission Security Desk procedures. |
| 2 | When a CSC limit changes, immediately change the limit in RTMONI. Record this event in the Transmission Security log. |

| ### 2.2.12 Post-Contingency Overload of the Sandow Autotransformer |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | To relieve the post-contingency overload of the Sandow autotransformer in the event that Sandow unit # 4 trips off line. OR If Sandow unit # 4 is off line and the Sandow autotransformer is overloaded. |
| 1 | Implement the appropriate action: - IF LAARs are available at Sandow, issue an OOME VDI to the Luminant QSE to deploy the MW amount of LAARs necessary to relieve the overload; up to the amount of LAARs scheduled by Luminant. - IF LAARs are not available at Sandow, instruct the ONCOR TSP to shed <amount> MW firm load in the MW amount necessary to relieve the overload. |
| 2 | IF LAARs were deployed in Step 1 AND the overload duration is expected to exceed 90 minutes, instruct the Luminant QSE to replace their RRS obligation from another source. |
| NOTE: | If needed, work with the TDSP/ appropriate entity if they request to rotate the deployed LAARs/firm load that was shed. |
| 3 | When the overload has been resolved AND system conditions permit, implement the appropriate action: - IF LAARs were deployed in Step 1, terminate the OOME VDI with the Luminant QSE. - IF firm load was shed in Step 1, instruct the ONCOR TSP to restore <amount> MW of firm load at Sandow. |

| ### 2.3.3 Maintenance Level 2 & 3 Outages |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Maintenance Level 2 and 3 outages are coordinated with the ERCOT Outage Coordination Group. These outages should not be “accepted” by anyone other than that group. However, until they are accepted in the Outage Scheduler, they will continue to show up every time the Outage Scheduler refreshes (that is about every two minutes). |
| 1 | DO NOT check the ‘accept’ box for Maintenance Level 2 & 3 Outages in the Outage Scheduler. Instead, place those Maintenance Level 2 & 3 Outages in ‘Study’ status and notify the Outage Coordination group of the Maintenance Level 2 & 3 Outage by sending an email to the ‘OPS Outage Coordination’ distribution list. |

| ### 2.3.8 Guidelines for Withdrawal of an Outage |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The system operator may WITHDRAW any: - approved or ACTIVE outage IF the security analysis and operator experience, or operator experience alone indicates the outage may have an adverse impact on system reliability. |
| 1 | IF an outage is withdrawn, ENTER an explanation in the “Reviewers Notes” listing the reliability concerns that caused the withdrawal. As soon as possible, NOTIFY by e-mail: - OPS Outage Coordination - OPS SUPPORT ENGINEERING Include in the e-mail: - From Station – To Stations (if applicable), - The Planned Start and Planned End Date of the outage |
| 2 | IF a TO or QSE reports that the outage in question has progressed to a point that withdrawal is not practicable within the outages designated restoration time, the System Operator shall: - Record this in the “Outage Scheduler Review’s Notes” - Log the outage in the Transmission Security Log - INFORM the Shift Supervisor and continue monitoring system security |

| ### 2.4.1 Respond to Voltage Issues |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | When a VDI is given requesting voltage support from a QSE, the VDI will direct the QSE to maintain a specified voltage set point. The VDI shall not attempt to quantify the change in generator MW output necessary to maintain the voltage set point. |
| NOTE: | In compliance with ERCOT protocols 6.5.6 and 6.5.7, ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found at: http://www.ercot.com/gridinfo/generation/voltprof/index.html |
| 1 | When indicated, by SCADA alarms or when notified by a Transmission Operator of voltage concerns, TAKE appropriate action. |
| 2 | Use displays that contain voltages that are of concern. |
| 3 | INITIATE a solution in collaboration with appropriate Transmission Operator and/or QSEs. |

| ### 2.4.2 Assist Transmission Operator with Voltage Issues at Nuclear Power Plant |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ERCOT and TDSPs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| 1 | WHEN notified by a Transmission Operator of an issue with the switchyard voltage at the South Texas Project or Comanche Peak, ENSURE voltage remains within the following limits: For Comanche Peak ###### System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141. - Tolerance; - +2.56% or –3.40%; - +2.13% or - -4.26%. - Maximum Voltage; - 361 kV; - 144. - Minimum Voltage; - 340 kV; - 135. For South Texas Project ###### System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +2% or -4%. - Maximum Voltage; - 369.5kV. - Minimum Voltage; - 347.8kV. |
| 2 | IF voltage exceeds maximum or minimum THEN COORDINATE with the Transmission Operator and QSE and DIRECT appropriate voltage control action. |
| NOTE: | Calaveras (Spruce, Von Rosenberg, etc), DOW, WAP, are points at which generation voltage adjustments can be expected to impact control of STP voltage. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. |

| ### 2.4.4 Power System Stabilizers (PSS) and Automatic Voltage Regulators (AVR) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ERCOT Protocol Section 6.5.7.2, QSE Responsibilities states that “…any QSE-controlled power system stabilizers will be kept in service unless specifically permitted to operate otherwise by ERCOT…” Operating Guide Section 2.2.4, Automatic Voltage regulators and Power System Stabilizers also states that PSSs must be in service whenever possible. The Transmission Operator shall know the status of all transmission Reactive Power Resources, including the status of voltage regulators and power system stabilizers (PSS). (VAR-001-1) (R6) Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes …a status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. (VAR-002-1) (R3.1) |
| NOTE: | QSE’s will inform ERCOT of a change in status with any PSS or AVR by phone. |
| 1 | The ERCOT Operator will: - Ensure that the QSE has notified the TO of the change in status. - Enter the status change information into the ERCOT Logs - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being taken out of service). - Cut and paste the log entry into an e-mail and send to “OPS Support Engineering” |
| NOTE: | Operations Planning will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at \\cpwp004d\departments\Operations Support\Operations Planning\AVR and PSS Status. |

| ### 2.5.5 Notification of Condition Termination |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Alert, Advisory, or Emergency Notice will constitute cancellation of the previous notification. |
| 1 | When the situation requiring the notification is relieved, NOTIFY Market Participants and Transmission Operators that the condition has been terminated. OCNs do not require “termination” notification. - Place termination time in ENS - Make Notices invalid in MIS - Initiate a hotline call to all Transmission Operators and QSEs (or see that another operator does so). - Print Hotline log and save in daily log as time permits |

| ### 2.5.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for conservation is enacted TO’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue if necessary until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |
| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MWs, OR - ERCOT has deployed over 760MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| 1b | Using the hotline, notify all TOs to implement EECP STEP 1. - Print the Hotline log Typical script: “ERCOT has implemented EECP STEP 1.” |
| 1c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor, as time permits. |
| 1d | Ensure the following is complete: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 2a | In addition to measures associated with STEP 1; Implement EECP Step 2 IF, - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| 2b | In conjunction with the ERCOT Frequency Control Desk Operator, implement EECP STEP 2. Using the hotline, notify all TOs to implement EECP STEP 2. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor, as time permits Typical script: “ERCOT has implemented EECP STEP 2; - LaaRs have been deployed - Within the time frame of the emergency, TOs that have the ability are to implement Block Load Transfers and transfer load from the ERCOT control area to Non-ERCOT control areas - If local operating conditions permit, TOs are to reduce customer loads by using distribution voltage reduction measures - Report back to ERCOT when these actions have been initiated and/or completed |
| 2c | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures that have been taken. |
| 2d | Unless a media appeal is already in effect, issue an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) Notify TO’s that a media appeal for conservation is in effect via Hotline. |
| 3a | In addition to measures associated with STEP 1 & 2; Implement EECP Step 3 IF: LAARs have been deployed AND EILS has been procured, AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| NOTE: | There are two separate blocks of EILS: The first is called EILS Business Hours: Business hours are defined as HE 0900- HE 2000 on Business Days Monday through Friday not to include Holidays. The second is called EILS Non-Business Hours: Non- Business Hours are classified as any hour not defined as Business Hours. When a deployment of EILS is implemented and the event is still in effect when one Time Period (either Business Hours or Non-Business Hours) ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. QSEs representing EILS Resources that are obligated in the new Time Period shall not deploy the newly obligated EILS Resources unless instructed to do so by ERCOT. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. When issuing a VDI for EILS specify Non- Business Hours or Business Hours in the Instruction Section of the VDI. |
| 3b | Using the hotline, notify all TOs to implement EECP STEP 3. When TOs have answered the Hotline, print the Hotline log and forward it to the Shift Supervisor, as time permits. |
| 4a | In addition to measures associated with STEP 1, 2 & 3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| NOTE: | Firm load is to be shed in 100 MW blocks. TOs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of EECP. |
| 4b | Using the hotline, notify all TOs to implement EECP STEP 4. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT has implemented EECP Step 4. ERCOT is instructing all Transmission Operators to shed their share of <amount> MWs. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load shed.” |
| 4c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor, as time permits. |
| 4d | Inform the Frequency Control Desk Operator that notifications have been completed to the Transmission Operators to shed firm load. |
| 4e | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures have been taken where possible - Load shed instructions have been received and enacted. |

| ### 2.5.7 Restore EECP Steps |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP Restoration. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| 4 | Begin restoring firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MWs |
| 4a | Using the hotline, notify all TOs of firm load restoration. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor, as time permits. Typical Script: “ERCOT is instructing all Transmission Operators to now restore their share of <amount> MWs leaving <amount> MWs still off. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load restored.” |
| 4b | Ensure the following: - “ERCOT is restoring firm load” is posted on the Emergency Notification System (ENS) short version – 32 characters - “ERCOT is restoring firm load” is posted on the Market Information System (MIS) |
| 4c | Maintain Adjusted Responsive Reserve supplied from generation equal to 1150 MWs while restoring firm load. |
| 4d | Ensure that the Frequency Control Desk Operator notifies the QSEs that firm load is being restored. |
| 4e | Move from EECP STEP 4 to STEP 3 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored |
| 4f | Using the hotline, notify all TOs of the reduction from EECP Step 4 to Step 3: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT is moving from EECP Step 4 to Step 3.” |
| 4g | Ensure the following: - EECP Step 4 to Step 3 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 4 to Step 3 is posted on the Market Information System (MIS) |
| 4h | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |
| 4i | When directed by the Frequency Control Desk Operator, use the hotline and notify the TOs that LaaRs are being restored. |
| 4j | Resend distribution voltage reductions measures as appropriate. |
| 3 | Move from EECP STEP 3 to STEP 2 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 3a | Using the hotline, notify all TOs of the reduction from EECP Step 3 to Step 2: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor as time permits. Typical script: “ERCOT is moving from EECP Step 3 to Step 2.” |
| 3b | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |
| 3c | Appeal through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisors procedures) |
| 3d | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |
| 2a | Move from EECP Step 2 to Step 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MWs, AND - All LaaRs have been restored, or replaced with generation. |
| 2b | Using the hotline, notify all TOs of the reduction from EECP Step 2 to Step 1: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor as time permits. Typical script: “ERCOT is moving from EECP Step 2 to Step 1.” |
| 2c | Ensure the following steps are complete: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters EECP Step 2 to Step 1 is posted on the Market Information System (MIS |
| 2d | If Block Load Transfers have been executed, restore them as system conditions permit. Typical Script: “TOs who have transferred load to Non-ERCOT control areas may restore such load as local conditions permit. Keep ERCOT advised on the progress and completion this task.” |
| 2e | Instruct the Frequency Control Desk to notify QSEs that BLTs are being restored. |
| 2d | Recall EILS. Maintain a minimum of 2300 MWs of Adjusted Responsive Reserve.. Move from EECP Step 1 to Termination when: - All EILS resources have been recalled, AND - All uncommitted units secured in EECP STEP 1 can be release to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 2e | - Using the Hotline notify the TOs that EILS is being recalled. |
| 1a | Move from EECP Step 1 to Termination when: - EILS resources have been recalled. AND - All uncommitted units secured in EECP STEP 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND Sufficient Regulation Service exist to control to 60 Hz. |
| 1b | Using the hotline, notify all TOs of the reduction from EECP Step 1 to termination: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor,as time permits. Typical script: “ERCOT is terminating EECP. An Alert still remains in effect.” |
| 1c | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |

| ###### Step # | ###### Procedural Steps |
| --- | --- |

| ### 2.6.6 Monthly Testing of Satellite Phone System |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Purpose: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| Note: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 2 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Attachment B of the ERCOT Satellite Phone User Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 3 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 4 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form (SEE Appendix 10). An electronic copy of this form is located in P:\ SYSTEM OPERATIONS ”Satellite Bridge Testing forms” folder. |
| 5 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is complete. |
| 6 | Log the test date and results in the ERCOT Operations Log. |
| NOTE: | Email Cagle Lowe regarding any Satellite phone problems during the test. |

## Appendix 3:  Conducting Security Analysis

NOTE:  Ensure that the OPF AND STCA Buttons are gray and only the PWRFLOW button is depressed (brown).  You must run a successful Power flow before doing Security/Contingency Analysis.

Load a Basecase (This gives you a starting topology to insert a generation plan, dynamic ratings, outages, and load against)

- Select EMP Applications pull down – Network Study Applications – Study Network Analysis

  - Make sure “Start Process” button is red lettered (select stop if necessary)

  - Select “Data Retrieval” button

  - Select “Save case Directory” button

  - From the “SAVECASE DIRECTORY” screen find the “Most Current” save case

  - Scroll down to the STNET Area, the “Most Current” Case will have several “x’s” following it. Example: OPS_01_01_06_XXXXXXXXXX.

  - Move the curser over the case you would like to retrieve.

  - Right Click for savecase options.

  - Select “retrieve” and acknowledge pop-up

  - Return to the “Network Study” Screen

  - Wait for a dialogue box to tell you that the case has been successfully retrieved – click OK

  - Select the “Start Process” button – it should be white when you are through

Generation Plan, Copy Dynamic Ratings, Load Current Hour Outages and Load Forecast for Desired Hour

- Select EMP Applications pull down – Network Study Applications – Study Network Analysis

  - Type in date and time for desired time in the “Time of Study” field (if you insert a minus sign “-” the current date and time will be inserted)

  - Click on “Stop Process”

  - Go to EMP Applications—Model Data Transfer

  - If prior to 1600, Select From Source to be “SE Solution” , otherwise select “Market Database”

  - Select To Destination to be “Study Network”

  - Verify “Remove Units that are not in the source” button is depressed (Tan)

  - Click “Copy Gen Plan” Wait for a dialogue box to tell copy is complete

  - Return to the “Network Study” Screen

  - Turn on GTs that are off-line, have a 30 minute or less lead time, and have their Non-Spin flag checked (Effective date June 12, 2007)

  - Click on “Start Process”

  - Ensure “Copy Dynamic Ratings” button is depressed

  - It may be desirable to run Powerflow at this time to ensure a valid starting point.

  - Ensure “Enable Outage Scheduler Interface” button is depressed

  - It is only necessary to import “Dynamic Ratings” and “Outage Scheduler” during the first run, then you may turn them back off (Grey)

  - Select “Run Solution Sequence” button. You should get a “Valid Solution” message in the “Process Status” field.

NOTE:  Turning on GTs that are off-line and have their Non-Spin flag checked, will make the study assumptions equivalent to the RPRS study assumptions.  The effects of the GTs on congestion in particular areas can be analyzed by running one study with the GTs and one without the GTs.  The off-line GTs can be utilized in real-time to resolve local congestion that is in close proximity.  These units will require an OOMC instruction in order to bring them on-line to resolve local congestion.  (Effective date June 12, 2007)

You have now loaded a Generation Plan, Outages and a Load Forecast for the hour you selected.

Under Related Displays go to Network Base Case Violations-- Branch Violations poke point to see where problems exist.

General Notes on Other Messages in the “Process Status” Field

NOTE:  Initially get help as needed from support personnel.  Experience is the best teacher.  As expertise is developed using this tool to “manipulate” and “massage” the power flow model will increase its accuracy.

- Case Diverged – Check outages, genplans, load forecasts and generation patterns against real-time flows (Under Analyst Displays Network Components check Unit Bus and Load Summaries)

- Maximum Iterations – Under Related Displays Power flow Solution Iterations –

This will identify substations with problems.  Usually, it’s voltage problems.  Check the station for high/low voltages.  Survey the grid to see where generation adjustments can be made or restore/remove capacitors and reactors as necessary.

Make additional changes to your case if needed before running Contingency Analysis

(This may be necessary in the case of forced outages that are not in the OS.  It’s a good idea to “turn-off” the Outage Scheduler at this point.  With the Outage Scheduler “on,” anytime you solve the case, any outage not scheduled will be restored.  You can also adjust generation)

NOTE:  If you don’t have any additional changes to make, skip this step and go to ‘Evaluate Contingency Analysis Result’ section.

- Select EMP Applications pull down – Network Study Applications – Study Network Analysis.

- Make any additional changes to base case by selecting the Related Displays pull down – Network Components.

  - Under Network Components –  Network Bus Summary is useful for removing lines

  - Network Breaker Summary is useful for changing breaker status

  - Network Load Summary can be used to move load and change flows

  - Complete necessary changes.

Evaluate Contingency Analysis Results

- Select Analyst Display pull down – Network Application Configuration.

  - Under Installation Flags make sure OS button is “off” (light colored)

  - Under Applications Characteristics check to see that DTS button is “off”

- Select EMP Applications pull down – Network Study Applications – Study Network Analysis.

  - Select Power flow and STCA buttons “on” and then select the “Run Solution Sequence” button.

  - “Complete” message in Process Status means that Contingency Analysis was successful

- Select Related Displays pull down – Contingency Analysis Displays – Contingency Violation Results (This screen gives you a complete overview of the results of the CA run).

  - Select any Contingency button to see respective results

- Select EMP Applications pull down – Network Study Applications – Study Network Analysis

  - Select Save Case Directory

  - Scroll down until the STNET list of cases is at the top of the page.

  - In the Command Line at the top of the display, enter the name of the case using the following example for Security Analysis Studies.

SC_011002_1630_EAV

SC designates a Security Analysis Case; the six-digit number is the DATE, the four-digit number is the time for which the study was run and the last letters are the initials of the person who ran the study.  All fields are separated by an underscore.

At the top of the STNET list, click the save button.

In approximately one minute, a message will appear acknowledging that the case was saved.

WITHDRAW APPROVED OUTAGES

If a pre or post-contingent violation can’t be cleared and an outage has been determined to be the cause, determine if the outage needs to be withdrawn. (Solicit advice from an Operations Engineer if needed.)

- If it is determined that the outage needs to be withdrawn but it has not started,

  - In the Outage Scheduler, change the status of the outage to WITHDRAWN.

  - Provide a brief explanation for withdrawing the outage in the ‘Reviewers Notes’ section.

  - Verbally notify the applicable Transmission Operator.

  - Notify by email OPS OUTAGE COORDINATION and OPS SUPPORT ENGINEERING

- Include:

- The From and To Stations (if applicable),

- The Planned Start and Planned End Date of the outage and the reason for withdrawing the outage

- If the outage has already started,

  - Determine, with the assistance of the Operations Engineer and/or the Shift Supervisor if the outage needs to be placed back into service.

  - If it is determined that the outage will be placed back into service,

- Call the applicable Transmission Operator and request the Transmission Operator put the equipment back in service.

- If the Transmission Operator can not comply with the request within the restoration time provided in the Outage Scheduler, refer to the Shift Supervisor for possible Incident Report (Protocol violation).

- If the Transmission Operator can comply with the request, in the Outage Scheduler, change the status of the outage to WITHDRAWN

- Provide a brief explanation for withdrawing the outage in the ‘Reviewers Notes’ section. (The Transmission Operator will enter the Actual End Time of the outage into the Outage Scheduler.)

- Notify by email OPS OUTAGE COORDINATION and OPS SUPPORT ENGINEERING

- Include:

- The From and To Stations (if applicable),

- The Planned Start and Planned End Date of the outage and

- The reason for withdrawing the outage

Evaluate Contingency Analysis Results

Select Analyst Display pull down – Network Application Configuration

NETWORK APPLICATION CONFIGURATION

Under Installation Flags make sure OS button is “off” (light colored)

Under Applications Characteristics check to see that DTS button is “off”

Select EMP Applications pull down – Network Study Applications – Study Network Analysis

NETWORK STUDY

Select Powerflow and STCA buttons “on” and then select the “Run Solution Sequence”

Button “Complete” message in Process Status means that Contingency Analysis was successful

Select Related Displays pull down – Contingency Analysis Displays – Contingency Violation Results

CONTINGENCY SOLUTION RESULTS

This screen gives you a complete overview of the results of the CA run

Select any Contingency button to see respective results

Select Related Displays pull down – Contingency Analysis Displays – Contingency Violation Results

CONTINGENCY VIOLATIONS

This screen gives you an overview of the contingencies that caused violations

Save Results

Select EMP Applications pull down – Network Study Applications – Study Network Analysis

DATA RETRIEVAL

Select Save Case Directory

Scroll down until the STNET list of cases is at the top of the page

In the Command Line at the bottom of the display, enter the name of the case using the followingexample for Security Analysis Studies

SC_011002_1630_EAV

SC designates a Security Analysis Case, the 6-digit number is the DATE, the four-digit number is the time for which the study was run and the last letters are the initials of the person who ran the study.  All fields are separated by an Underscore.  At the top of the STNET list, poke the save button.  In approximately one minute a message will appear acknowledging that the case was saved.