Power Operations Bulletin # 364

ERCOT has revised the Shift Supervisor Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

### ERCOT System Operator Responsibility and Authority

The System Operator (SO) shall, in accordance with NERC Standard PER-001, have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System during both normal and emergency conditions.

The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Standards the Balancing Authority, Transmission Operator,  and Regional Reliability Coordinator and shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

The SO shall review the ERCOT Daily Operations Plan (DOP) and calculate and post the Allocated Responsive Reserve and other Ancillary Services Obligations.  The SO shall ensure compliance with the ERCOT Protocols and Operating Guides on identified transfer limits.  The SO receives all specified notifications for the MPs with regard to energy transactions (Balanced Schedules), AGC control modes, routine adjustments, and equipment limitations or outages.

The SO processes all Balanced Schedules and Resource Plans. The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Assistance over the DC Tie(s) on behalf of ERCOT.

The SO shall issue appropriate advisories and alerts, emergency notices, and coordinate the reduction or cancellation of clearances, redispatch generations, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Standards.

- The SO will implement and terminate ERCOT Time Corrections.

- The SO will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s frequency control system.

| ### Disseminating Information |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The SSRG e-mail exploder list is used to disseminate information to the SSRG members of the ERCOT Region when an SSRG conference call is not necessary. |
| NOTE: | The Reliability Coordinator Information System (RCIS) is used to disseminate information to other RCs in NERC. |
| 1 | Once notified by a QSE or TO of an incident, send an SSRG e-mail and post on the RCIS. These types of incidents could include but are not limited to the following: - Copper thefts - Substation break-in - Vandalism - Malicious mischief - Suspicious photos |
| NOTE: | When posting on the RCIS, use the “CIP Free form” to post anything out of the ordinary, threats, or thefts when you can reasonably assume the event not to be related to terrorist type activities. Use the “DHS form” whenever an event, threat (cyber or physical), surveillance, or any other activity that can or might be terrorist-related. |

# Control Center Supervision Duties

## Providing Technical & Operational Support

The Shift Supervisor is responsible for ensuring operations are in compliance with ERCOT Protocols, NERC Standards, Operating Guides, and Operating Procedures.  The Shift Supervisor must have a very good understanding of the ERCOT Protocols, Operating Guides, and NERC Standards.

The Shift Supervisor may consult with Operations Support, Operations Planning, Market Operations, or any resource he deems necessary to resolve and clarify market related issues.  He/She will assist the System Operators in resolving market issues.

The Shift Supervisor also monitors and ensures that adequate coordination between the ERCOT Control Center and the neighboring Balancing Authority (BA) and Reliability Coordinator (RC) is maintained.  To this effect the Shift Supervisor monitors the communications and coordination between the DC-Tie Desk and the neighboring BA and RC.

The Shift Supervisor is responsible for running primary operations from the Backup Control Center once per month.  This is to ensure all desks are functional in the case of an emergency.

The Shift Supervisor has the authority to coordinate additional support to assist during emergencies, system and weather related disturbances, and high demand periods as deemed necessary.  Support may be required from Operations Support, Operations Planning, Market Operations, Outage Coordinators, and System Operators assigned to the Backup Control Center.  The Shift Supervisor also has the authority to assign temporary duties to this additional support staff.

Finally, other Shift Supervisor duties may require the on-shift Shift Supervisor to leave the Control Center from time to time.  On these occasions, the Shift Supervisor may delegate his duties to another system operator on a temporary basis.  The Shift Supervisor shall remain in contact and accessible to the control center via available communication means.

| ### Supervise Coordination with the Neighboring BA and RC |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The coordination with the neighboring BA and RC is the responsibility of the System Operator on the DC-Tie desk. This coordination is required due to the use of the DC-Ties as described in the DC-Tie desk procedures and ERCOT Operating Guides. The ERCOT Shift Supervisor is responsible for ensuring that those duties related to NERC Tagging and Interchange Scheduling through the DC-Ties are carried out per the procedure. |
| 1 | CONFIRM with the DC-Tie desk Operator that DC Tie schedules and NERC Tags were properly verified. |
| 2 | Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities, per the procedure. |

| ### Monitoring CSC Limits |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | NERC Standard TOP-004-0 states to ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | If necessary, near the end of each shift, verify that the CSC Limits have not been exceeded during the shift. - Open PI Process Book - Select Transmission Limit & Flow Summary for the ERCOT Top Page tab. - Check each CSC flow during the desired date range - Select Calendar to change the date range (The display will graph the CSC limit and line flow for that date range) - Deselect first flow and check next flow - Continue until all flows have been selected and all data has been collected. |
| 2 | If any CSC exceeds the limit for more than 30 consecutive minutes: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. - Save the study in the STNET directory. |
| 3 | Notify by e-mail (including data from Step 2) - Manager, System Operations - Ops Support Engineering - Beth Garza - Isabel Flores |

| ### Monitoring Market Clearing Prices |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | . - IF a constraint becomes “ACTIVE”, verify that the Transmission & Security Desk Operator is monitoring it and that it is not being over constrained - IF the Zonal pricing shows to be abnormally high or low, check market conditions for that interval to insure that there is a sufficient amount of Balancing Energy, AND that the Balancing Offset is reasonable |

| ### 2.2 Responding to System Disturbances |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The system operators on the Transmission & Security, Frequency Control, and DC-Tie desk normally handle system disturbances. |
| 1 | The Shift Supervisor will monitor, assist and/or assign additional staff as needed to respond effectively to system disturbances. |
| 2 | If system disturbance was a possible DCS event, ensure that the Contingency Reserves are restored within 90 minutes |

| ### 2.2.1 Supervise Response to Major System Disturbances |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | NERC Standard BAL-002-0 R6 states that a Balancing Authority shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. R6.1. The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. R6.2. The default Contingency Reserve Restoration Period is 90 minutes. |
| 1 | IF the system disturbance cannot be normalized with current on-shift staff, THEN IDENTIFY and ASSIGN additional System Operators, Operations Support, Operations Planning, or Market Operations staff to assist in normalizing the system condition. |
| 2 | The ERCOT Shift Supervisor will ACT as the main contact and answer inquiries between the control room and other ERCOT operations groups during system disturbances. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Appendix 1 of this procedure. |
| NOTE: | See Phone Book at Shift Supervisor’s Desk. |

| ### Gas Restriction Notifications |  |
| --- | --- |
| 1 | Once notified by a QSE of gas restrictions, send an e-mail to “Gas Restriction Notification”. This will notify all appropriate ERCOT staff. |
| 2 | Ensure gas restriction will not cause ERCOT reliability issues. Follow the necessary procedures. |

| ### 2.2.8 Initiate Request for Public Appeals |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| CAUTION | Prior to entering EECP, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Officer or its designee based on an evaluation of existing and expected system conditions. |
| NOTE: | See Appendix 2 “Media Appeals for Voluntary Load Curtailments”. |
| NOTE: | See Phone Book at Shift Supervisor’s Desk. |
| NOTE: | The EECP procedures are coordinated between the system operators on the Transmission and Security, Frequency Control and DC-Tie desk. |
| 1 | WHEN the EECP procedures are invoked, at your discretion or in no case later than STEP 2 of the EECP, INITIATE a request for a public appeal for voluntary load reduction. See Appendix 2 “Media Appeals for Voluntary Load Curtailments” for notification guidelines. |
| 2 | As part of Restoration STEP 2 of the EECP procedure you may RECALL the request for a public appeal for voluntary load reduction. When the decision is made to RECALL the voluntary load reduction, See Appendix 2 “Media Appeals for Voluntary Load Curtailments” for notification guidelines. |

| ### 2.2.9 Issue System Operations Notifications |  |
| --- | --- |
|  | ###### Procedural Steps |
| NOTE: | Complete the following steps when a significant amount of firm load is shed in ERCOT that is not related to EECP Step 4: |
| 1 | Have the Transmission and Security Desk make a Hotline call to TOs within 30 minutes with the firm load shed information. |
| 2 | Have the Frequency Control Desk make a Hotline call to the QSEs within 30 minutes with non-market sensitive information. |

| ### 2.2.11 NERC and DOE Disturbance Reporting |  |
| --- | --- |
|  | ###### Procedural Steps |
|  | When Disturbance reporting is required: |
| NOTE: | NERC E-mail address: esisac@nerc.com, fax (609) 452-9550 DOE E-mail address: doehqeoc@oem.doe.gov, fax (202) 586-8485 DOE Operation Center voice phone: (202) 586-8100 |
| NOTE: | Disturbance Reporting requirements can be found in NERC Standard EOP-004-1. The DOE EIA-417 Schedule 1 report and NERC Preliminary report are to be filed within 1 hour after the start of the incident or disturbance. The Operations Support Engineering group will follow-up with the DOE EIA-417 Schedule 2 report and NERC Final report. |
| 1 | Forward the TSP(s) report or the Director of Cyber Security’s report to NERC, DOE, and the “NERC and DOE Disturbance Reporting” e-mail list. Ensure all three entities receive the report. (e.g. If TSP or Director, Cyber Security sends a report to only one entity; make sure the other two entities receive the report as well.) |
| 2 | If ERCOT is required to issue a report to NERC and DOE even when the disturbance does not require a report from a TSP (e.g. The disturbance involves two or more TSP areas to meet the requirements for reporting.) or if a report is received from the Director, Cyber Security, then do the following: - Complete required NERC report per Attachment 1-EOP-004. - Complete required DOE OE-417 Schedule 1 report. - Forward reports to NERC, DOE, and the “NERC and DOE Disturbance Reporting” e-mail list. |
| NOTE: | NERC report forms can be downloaded at ftp://www.nerc.com/pub/sys/all_updl/standards/rs/EOP-004_NERC_IROL_and_Preliminary_Disturbance_Report.doc DOE OE-417 report forms can be downloaded at ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. |
| NOTE: | A guideline on “Threat and Incident Reporting” can be found at “www.esisac.com” |

| ### 2.2.12 PUC Daily Report |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The PUC reports are to be generated twice per day: In winter months at 0100 and 0500 In summer months at 1100 and 1500 The timing change will be determined by the Manager, System Operations. |
| NOTE: | Be able to provide a list of unplanned generation outages for the day if requested by the PUC. |
| 1 | Complete the PUCT Daily Report template at the appropriate times. E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Do not add editorial comments to this report that reveal market sensitive data. General comments that convey overall system conditions are allowed. |
|  | Revise the last report sent and resend it if: - The probability of an EECP event increases. Give reason(s) for escalation, OR - Conditions change that required new notices to be issued or cancelled, such as, an OCN , Advisory, Alert, or Emergency Notice OR - A shortage of generation capacity develops OR - Local reliability concerns arise which include actual overloads and/or loss of load, especially the Laredo area, OR - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if there are unplanned outages of the generation units in the area. - Localized gas restrictions, not expected to cause reliability issues. - DCS event occurs - “ERCOT only” NERC and/or DOE event occurs. These events are market sensitive so provide a brief description without the market sensitive information. |
| 2 | Use the following guidelines to determine the potential for EECP when completing the PUCT Daily Report: Potential for EECP 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves. - Medium - An Alert is in effect for Adjusted Responsive Reserves. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - High - An Alert is in effect for Adjusted Responsive Reserves and trending downward after procuring quick-start capacity. - Critical - EECP Step 1 in effect |
|  | Potential for EECP 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves - Medium - EECP Step 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EECP Step 2 in effect |
| 3 | Potential for EECP 3 - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EECP Step 2 in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EECP Step 3 in effect |
| 4 | Potential for EECP 4 - Low - Sufficient capacity to cover peak demand - Medium - EECP Step 2 in effect - High - EECP Step 3 in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EECP Step 4 in effect |
| NOTE: | When conditions have returned to normal, update report and e-mail. |

| ### 2.2.13 Geomagnetic Disturbance Reporting |  |
| --- | --- |
|  | ###### Procedural Steps |
| NOTE: | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Enter the information into the MOI Emergency Notification System - Log the information. |

| ### 2.2.15 EECP/EEA (Energy Emergency Alert) Reporting |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Posting Energy Emergency Alerts (EEA) on the NERC Reliability Coordinator Information System (RCIS) There are four levels: EEA Alert 0: All previous alerts have been terminated and the entity can supply all energy requirements. Equivalent to Termination of EECP Steps. EEA Alert 1: The entity foresees or is experiencing conditions where all available resources are committed to meet firm load, AND is concerned about maintaining its required Operating Reserves. Equivalent to EECP Step 1. EEA Alert 2: The entity can no longer provide expected energy requirements and foresees or has implemented procedures up to, but excluding, shedding firm load. Equivalent to EECP Step 2 and Step 3. EEA Alert 3: The entity foresees or has implemented firm load shed. Equivalent to EECP Step 4. You may declare whatever alert level is necessary, and need not proceed through the alerts sequentially. Reference NERC Standard EOP-002-2 Capacity and Energy Emergencies for detailed information. |
| 1 | If EECP step 1 is implemented, post following message to RCIS: “ERCOT is declaring EEA Alert 1 due to <brief description of emergency condition>.” |
| 2 | If EECP step 2 or step 3 is implemented, post following message to RCIS: “ERCOT is declaring EEA Alert 2 due to <brief description of emergency condition>.” |
| 3 | If EECP step 4 is implemented, post following message to RCIS: “ERCOT is declaring EEA Alert 3 due to <brief description of emergency condition>.” |
| 4 | When recalling EECP/EEA, reverse the order and make the appropriate RCIS postings. When the emergency condition has been terminated, post EEA Alert 0 (zero) to terminate all previous NERC EEAs. |
| NOTE: | Progression to EEA Alert 3 requires filing a report with NERC in addition to the RCIS posting. The report (Energy Emergency Alert 3 Report) can be obtained from the following link: ftp://www.nerc.com/pub/sys/all_updl/alertlogs/Energy_Emergency_Alert_3_Report_Form.doc |
| NOTE: | Refer to Table 2: ERCOT EECP and NERC EEA Notification Requirements. |

## Monitoring Real-Time Performance of QSEs

Monitoring of real-time performance of QSEs for system security purposes is a primary duty of the Frequency Control Desk operator.

The Shift Supervisor assists the Frequency Control Desk operator to perform this monitoring duty when a QSE(s) continually under perform during the same shift or Operating Period causing ERCOT’s overall performance to deviate from NERC standards.

| ### Monitor QSEs Which Under Perform in Supplying Ancillary Services |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | REVIEW the QSEs real time performance summary display periodically or when ERCOT ACE deviation is significant. Reference Displays: “ERCOT Responsive, Regulation, and SCE” display (EMS) |
| 2 | CONSULT with the Frequency Control Desk operator when abnormal real time performance by one or more QSEs is detected. |
| 3 | VERIFY if the Frequency Control Desk operator has established communication with the QSE(s) and the cause for the under performance is known. |
| 4 | VERIFY that the Transmission & Security Desk and Operation Period Desk operator is informed of the situation. |
| 5 | ALLOW the Transmission & Security and Frequency Control Desk operators to RESOLVE the problem and RESTORE ERCOT ACE performance to normal. |
| 6 | If a QSE(s) continues to under perform in real time, and ERCOT’s NERC performance requirements are not being met, ASSIGN a system operator to collect performance data on the QSE(s) affecting ERCOT’s NERC performance. |

| ### 2.4.3 Procedure for Possible Protocols and Operating Guides Violations |  |
| --- | --- |
| NOTE: | In the event that the Shift Supervisor believes a QSE or TO is in violation of the ERCOT Protocols or Operating Guides, he or she will take the actions listed in the steps below. |
| 1 | Verify that the system operators have verbally tried to persuade the QSE or TO personnel to correct those actions which are in violation. |
| 2 | The Shift Supervisor should attempt to resolve the issue verbally. Use Market Operations Support and/or Operations Support personnel, if needed, for information gathering. |
| 3 | If no agreement can be reached; review the incident to be sure there has been a violation.. |
| 4 | Find the appropriate section of the Protocols or Guides. |
| 5 | Complete a TRE Complaint Form located at http://www.ercot.com/mktrules/compliance/tre/enforcement/form/Texas%20RE%20Complaint%20Form.doc and SUBMIT the report to the Manager, System Operations for review and approval. |
| 6 | Log the Incident Report in the Shift Supervisors log. |

| ### Prepare Daily Operations Report |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The daily report is in a web base application, which is intended to create a report for the Public Utility Commission on a daily basis.. |
| 1 | Section 1: Index Enter the Peak Load, Time of Peak Load, Planned Peak Load (from the day ahead plan off of the Day Ahead desk), and time of planned peak |
| 2 | Section 2: Constraints Encountered During the Day Transmission Loading Actions the date will automatically be copied from Section 1. For each constraint activated in the model (by changing the limit or start times) a record should be placed in this section. DO NOT PLACE REPEATED ENTRIES FOR REPEATED STARTS AND STOPS OF CONSTRAINTS DURING THE DAY. Only enter a constraint once. VDI’s and OOME instructions should also be entered in this section as follows. Time: Interval Ending Constraint: A brief name of the constraint, or For OOME a statement of what was OOMd and what direction (up or down) or For VDI’s a statement of the VDI. Examples: Jewett - TH Wharton OC3; OOME XXX up; VDI XXX down Reason: A description of what element or limit was loaded, what the loading and percentage was when the action was taken, and what the limit was when taken. Example: Loss of Jewett -TH Wharton and Tomball 345KV overloads Watson Chapel - Robertson 138KV - 110% of 105 MVA rating. |
| 3 | Section 3: Other Notable Events - A description of any Alert, OCN’s, Advisories, and Emergency notices issued to the market. A description of any frequency deviations over .1 hertz including unit trips. A description of any market extensions or delays or equipment failures affecting ERCOT’s ability to deploy services or control the system. |

| ### Root Cause Analysis |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ###### The following events will trigger an investigation: - Possible violation of DCS Criteria - Frequency deviation of +/- .05 from scheduled frequency for greater than 30 minutes - High frequency events greater than 60.175 Hz. - Incorrect procurement/deployment of NSRS - OC1 constraint operation that depletes the Balancing Market (for more then one interval). - Operating actions outside of the ERCOT Protocols, Guides, Operating Procedures or NERC Standards - Over constraining - A constraint that remains active with no corresponding congestion - Anytime an OC1 remains active for more than two intervals, it was below 90% of the limit and no action was taken - An OOME or VDI with no corresponding congestion, import, or voltage concerns The Manager, System Operations may direct the investigation of other events not listed above. |
| NOTE: | ###### The “rule of thumb” is to ask why until the most basic cause of the problem is revealed. |
| 1 | ###### When an event occurs, notify the Manager, System Operations via e-mail that an investigation has been initiated. Include the event, time, duration, and a summary of what occurred. |
| 2 | Preserve all data relevant to the event: - EMMS data - Operational logs - Applicable graphs and charts |
| 3 | Evaluate the following conditions: - Resources - Software performance - Man – Machine interface - Procedures - Management directives - Training - Computer (hardware) performance - External Distracters - Control Room conditions - Market conditions - System conditions - Human Performance - QSE input and communication - TO input and communication - ERCOT internal support and communication - Shift communication and team work |
| 4 | A preliminary report is due within three days. The report should include: - A summary - The chain of events and/or decisions that produced the outcome - The most basic root cause - Recommended steps to prevent future events from occurring. |
| 5 | Forward the report and related information to the Manager, System Operations; keep one for the later discussion. |
| 6 | The Manager, System Operations will review the report with the appropriate ERCOT staff t and Shift Supervisor to identify the cause and recommend corrective action.. |

| ### 2.6.1 Report Critical EMMS Failures to ERCOT IT Help Desk |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | ACKNOWLEDGE computer system alarms, events, failures, or incidents that affect normal operations. |
| 2 | CONTACT the ERCOT IT Help Desk immediately from the Shift Supervisor Turret Phone preprogrammed number or extension 6804. |
| NOTE: | If necessary, contact the on-call IT person first then contact the Help Desk. |
| 3 | DISCUSS alarms, events, failures, or incident with the Help Desk or IT staff. |
| 4 | DETERMINE criticality and impact of the system alarms, events, failures, or incident jointly with the Help Desk or IT staff. |
| 5 | IF the criticality and impact of the system alarms, events, failures, or incident is such that Market Operations are or will be affected before the problem can be resolved, Notify market participants of the problem and expected duration via HOTLINE and REQUEST additional assistance from other support staff. OTHERWISE go to step 6. |
| 6 | RECORD the following in the shift log: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |
| 7 | When a critical problem affecting market participants is resolved, NOTIFY all participants via HOTLINE of the problem resolution. |

| ### 2.6.2 Reporting RTUs, ICCP, Web Portal, and API Failures |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | ACKNOWLEDGE RTU, ICCP, Web Portal or API alarms, events, failures, or incidents that affect normal operations. |
| 2 | CONTACT the ERCOT IT Help Desk immediately from the Shift Supervisor Turret Phone preprogrammed number or extension 6804. |
| NOTE: | If necessary, contact the on-call IT person first then contact the Help Desk. |
| 3 | DISCUSS alarms, events, failures, or incident with the Help Desk or IT staff. |
| 4 | DETERMINE criticality and impact of the alarms, events, failures, or incident jointly with the Help Desk or IT staff. |
| 5 | If it is determined that the Web Portal will be unavailable for longer than 15 minutes, have the QSEs and TOs notified by a hotline call. Include in the message: - The estimated duration of the portal unavailability - Any actions the TOs and QSEs should take |
| 6 | IF the criticality and impact of the alarms, events, failures, or incident is such that Market Operations are or will be affected before the problem can be resolved, Notify market participants via the Hotline of the problem and REQUEST additional assistance from other support staff. OTHERWISE, go to step 7. |
| 7 | RECORD the following in the shift log: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |
| 8 | When a critical problem affecting market participants is resolved, NOTIFY all participants via HOTLINE of the problem resolution. |

| ### 2.7.4 Emergency Evacuation |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Note: | The evacuation procedures will be practiced at least annually. The Shift Supervisor will not have advance notice of this training session. |
| Note: | Imminent danger examples are listed, but not limited to the following: - Bomb threats - Chemical spills - Chemical or biological attacks - Hostage situation It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of control room personnel. |
| 1 | If an unconfirmed threat exists, go to Step 4, otherwise continue; Upon confirmation of imminent danger to control room personnel immediately evacuate the control room to a secure area, taking the control room cell phone and a copy of this procedure with you. Notify ERCOT Security. Then go to Step 2. - ERCOT Security extensions: TCC1 – Ext. 7000 TCC2 – Ext. 6400 ACC – Ext. 3000 |
| 2 | Direct the Backup Control Center to perform the following: - Monitor the system until additional staff can arrive. - Place a Hotline call to QSEs and TOs notifying them that the ERCOT Primary control center has been evacuated and to report any reliability issues to the backup control center. |
| 3 | Notify the following: - Manager of System Operations - EMS Support - Engineering Support - NERC - Call out shift personnel to staff the backup site, including a Shift Supervisor, unless Primary Control Center shift will be relocating from the primary control center to the Backup Control Center. These phone numbers have been programmed into the control room cell phone. |
| 3 | If an unconfirmed threat exists, perform the following as a precautionary measure: - Call out shift personnel to staff the backup site, including a Shift Supervisor - Notify: - Manager of System Operations - ERCOT Security - EMS Support - Engineering Support - NERC |
| 4 | Evacuate to a safe area. |

| ### Catastrophic failure of EMMS |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | This scenario could only occur with the loss of both the Taylor EMMS A & B servers and Austin C & D servers. |
| 1 | CONTACT the ERCOT IT Help Desk immediately from the Shift Supervisor Turret Phone preprogrammed number or extension 6804. |
| NOTE: | If necessary, contact the on-call IT person first then contact the Help Desk. |
| 2 | Direct the Frequency Desk operator to perform the following: - Make a hot-line call to QSE’s to notify them of the catastrophic loss of the EMMS. Instruct QSE’s to hold last Base Power schedules and last good interval - Request a large QSE (that has regulation reserve) to be placed on constant frequency control - Issue fleet VDI’s if QSE on constant frequency needs assistance controlling frequency |
| 3 | Direct the Transmission and Security Desk to perform the following: - Make a hotline call to TO’s to notify them to the catastrophic loss of the EMMS. Instruct them to notify ERCOT of any transmission reliability issues. |
| 4 | Notify the following: - Manager, System Operations - Operations Support - Market Operations - Backup control center operator |

| ### Emergency Evacuation and Catastrophic EMMS Failure |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | It may be necessary for the Backup Control Center to carry out this procedure if no communication is coming from the Shift Supervisor. |
| 1 | Upon confirmation of imminent danger to control room personnel and a catastrophic EMMS failure, immediately evacuate the control room to a secure area, taking the cell phone and a copy of this procedure with you. |
| 2 | Direct the Backup Control Center to perform the following: - Make a hot-line call to QSE’s to notify them of the catastrophic loss of the EMMS and primary control center. Instruct QSE’s to hold last Base Power schedules and last good interval - Request a large QSE (that has regulation reserve) to be placed on constant frequency control - Make a hot-line call to TO’s to notify them to the catastrophic loss of the EMMS and Primary Control Center. Instruct them to notify ERCOT of any transmission reliability issues. - Issue fleet VDI’s if QSE on constant frequency needs assistance controlling frequency - Monitor the system until additional staff can arrive. |
| 3 | CONTACT the ERCOT IT Help Desk or, if necessary, the Manager, EMMS Production directly. |
| 4 | Notify the following: - Manager of System Operations - EMS Support - Engineering Support - NERC - Call out shift personnel to staff the Backup Control Center, including a Shift Supervisor, unless the Primary Control Center shift will be relocating from the Primary Control Center to the Backup Control Center. These phone numbers have been programmed into the control room cell phone. |

| ### 2.7.8 Monthly Testing of Satellite Phone System |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, test the Satellite Phone System with Transmission Operators to determine whether or not ERCOT has communication capability via the Satellite Phone System. |
| Note: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for instructions on how to place a satellite phone call. |
| 2 | - Call each Transmission Service Provider using the preprogrammed number on the Turret Phone. Refer to page #2 of the ERCOT Satellite Phone User Guide for instructions. If there is no answer: Call the Transmission Service Provider directly using the Satellite Phone number provided in Attachment A of the ERCOT Satellite Phone User Guide. - As contact is made with each Black Start Transmission Service Provider, (as listed in Attachment A of the ERCOT Satellite Phone User Guide) establish a time when a Satellite Conference Bridge Call will be made from the appropriate ERCOT Operations Desk. Refer to Attachment B of the ERCOT Satellite Phone User Guide for a list of Transmission Operators, Satellite phone numbers and Moderator Pass Codes for each ERCOT Operations Desk. |
| 3 | When testing is completed by all desks, fill out Monthly Satellite Testing forms located in P:\ SYSTEM OPERATIONS “Satellite Testing Phone Testing Forms” folder. |
| 4 | Email a copy to Manager, System Operations; All Shift Supervisors, and file a hard copy in the control room. |
| 5 | Log the test date and results in the Shift Supervisors Operations Log. |
| NOTE: | Send an e-mail to “1 ERCOT Training Department” for any Satellite phone problems during the test. |
| NOTE: | Not all Transmission Operators have satellite phones, so the call will be coming in on their regular landlines. You may verify whether or not they are communicating via satellite phone or regular landlines while testing. |

## Administrative & Supervisory Duties

| ### 2.8.2 Review Outages List |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | NAVIGATE to the daily operation plan in the MMS. Reference Displays: “DAILY OPERATIONS PLAN” display (MMS) or the ERCOT Outage Scheduler: https://mostml.ercot.com/outages_prp/default.cfm |
| 2 | ENTER or VERIFY the current market date. |
| 3 | LOCATE and SELECT the “Outage Schedule” tab on the display. |
| 4 | REVIEW the list of generation and transmission outages schedule for the current operating day. |
| 5 | Using the Outage Scheduler, verify if resources or facilities reported as Forced Outages are included in the outage list. |
| 6 | If Forced Outages are not listed, NOTIFY the Transmission and Security desk operator. |
| 7 | VERIFY with the Transmission and Security and Operating Period Desk operators the results of studies for the hours and zones where these resources and facilities are scheduled to be out of service. |
| 8 | IF errors or problems are detected, have the Transmission and Security and Operating Period Desk operators consult with the Outage Coordinator. |

| ### 2.8.3 Review Planned Reserves |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | NAVIGATE to the generation reserves display in the EMS. Reference Displays: “GENERATION AREA STATUS” display (EMS) |
| 2 | LOCATE the “Reserve Status Summary” on the page. |
| 3 | REVIEW the summaries for “System Current” and “System Required” reserves by reserve type. |
| NOTE: | Details for “System Available” and “System Requirements” are also available by QSE and unit if needed. |
| 4 | NAVIGATE to the QSE Reserve Status display in the EMS. |
| 5 | Check Generation, Responsive Reserve, Balance UP, Balance Down, Regulation UP, Regulation Down, and compare with Generation Reserve Status display. |
| NOTE: | May also want to compare with MAI. |
| 6 | IF errors or problems are detected, CONSULT with the Frequency Control and Operating Period Desk operator. |