Power Operations Bulletin # 365

ERCOT has revised the Shift Supervisor Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

### 1.3.2  ERCOT System Operator Responsibility and Authority

English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Standard PER-001, have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System during both normal and emergency conditions.

The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Standards, the Balancing Authority, Transmission Operator, and Regional Reliability Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

The SO shall review the ERCOT Daily Operations Plan (DOP) and calculate and post the Allocated Responsive Reserve and other Ancillary Services Obligations.  The SO shall ensure compliance with the ERCOT Protocols and Operating Guides on identified transfer limits.  The SO receives all specified notifications for the MPs with regard to energy transactions (Balanced Schedules), AGC control modes, routine adjustments, and equipment limitations or outages.

The SO processes all Balanced Schedules and Resource Plans. The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Assistance over the DC Tie(s) on behalf of ERCOT.

The SO shall issue appropriate advisories and alerts, emergency notices, and coordinate the reduction or cancellation of clearances, redispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s frequency control system.

As the Reliability Coordinator, ERCOT shall comply with its regional reliability plan that has been approved by the NERC Operating Committee.

The North DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent procedures and emergency procedures.

| ### 2.1.8 Supervise Coordination with the Neighboring BA and RC |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The coordination with the neighboring BA and RC is the responsibility of the System Operator on the DC-Tie desk. This coordination is required due to the use of the DC-Ties as described in the DC-Tie desk procedures and ERCOT Operating Guides. The ERCOT Shift Supervisor is responsible for ensuring that those duties related to NERC Tagging and Interchange Scheduling through the DC-Ties are carried out per the procedure. |
| 1 | CONFIRM with the DC-Tie desk Operator that DC Tie schedules and NERC Tags were properly verified. |
| 2 | Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities, per the procedure. |
| 3 | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operators and SPP or CFE. A message must also be posted on the MIS. |

| ### 2.2.1 Supervise Response to System Disturbances |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | NERC Standard BAL-002-0 R6 states that a Balancing Authority shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. Contingency Reserves must be restored within 90 minutes. The restoration period begins at the end of the disturbance recovery period. |
| 1 | IF the system disturbance cannot be normalized with current on-shift staff, THEN IDENTIFY and ASSIGN additional System Operators, Operations Support, Operations Planning, or Market Operations staff to assist in normalizing the system condition. |
| 2 | The ERCOT Shift Supervisor will ACT as the main contact and answer inquiries between the control room and other ERCOT operations groups during system disturbances. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Appendix 1 of this procedure. |
| NOTE: | See Phone Book at Shift Supervisor’s Desk. |

| ### 2.7.5 Critical Data and/or Voice Communication Failures |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | NOTIFY the Help Desk of the loss and request assistance to re-establish voice and/or data communications. The EMMS Production group will be responsible for data communications and the Telecommunications group will be responsible for voice communications. |
| 2 | Use back-up communications if available, if not, use cell phone to maintain communications with TO, QSE, SPP and any other entities as needed (NERC, PUCT, etc). |
| 3 | IF the criticality and impact of events, failures, or incidents is such that Market Participants are or will be affected before the problem can be resolved, notify all market participants via HOTLINE or cell phone of the problem and expected duration. REQUEST additional assistance from other support staff. |
| 4 | If data failure, follow step 4 in section 2.6.6. TO control centers can be reached on the ERCOT Black Start Satellite phone or cell phone. |
| 5 | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |
| 6 | When a critical problem affecting market participants is resolved, NOTIFY all participants via HOTLINE of the problem resolution. |
| NOTE: | See Phone Book at Shift Supervisor’s Desk. |

| ### 2.7.6 Loss of Primary Control Center Functionality |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | In the case that the primary control center becomes inoperable, all operations shall be transferred to the back-up control center. The Training Department shall be responsible for providing annual training to ensure that operating personnel are able to implement the contingency plan. Periodic tests, at least annually must be conducted to ensure viability of the plan. . |
| NOTE: | In the case that data and/or voice communication from the primary control center are not functioning, see procedure 2.6.1. |
| NOTE: | It is not expected to take more than one hour to implement the contingency plan for loss of primary control center. However, the interim provisions in this procedure must be performed to ensure the reliability of the ERCOT Grid. |
| NOTE: | Step 4 of this procedure will also be followed for a catastrophic failure of the EMMS System. |
| NOTE: | This section shall be reviewed and updated as necessary to meet ERCOT Protocols, Operating Guides, and/or NERC Reliability Standards requirements, but must be reviewed at least once a year. Last Review Date: February 11th, 2008 |
| 1 | Loss of primary control center could be due to imminent danger. Examples are listed, but not limited to the following: - Bomb threats - Chemical spills - Chemical or biological attacks - Hostage situation It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of control room personnel. |
| 2 | If threat is unconfirmed, call additional operators to staff the backup in case evacuation is needed. Once threat is confirmed, proceed to step 3. |
| 3 | Upon confirmation of imminent danger to control room personnel immediately evacuate the control room to a secure area, taking the control room cell phone and a copy of this procedure with you. Notify ERCOT Security. ERCOT Security extensions: TCC1 – Ext. 7000 TCC2 – Ext. 6400 ACC – Ext. 3000 |

| 4 | Direct the Backup Control Center operator to this procedure to perform the following: - Request a large QSE (that has regulation reserve) to be placed on constant frequency control. - Issue fleet VDI’s if QSE on constant frequency needs assistance controlling frequency. - Place a Hotline call to QSEs and TOs notifying them that the ERCOT Primary control center is inoperable and issue them the following instructions. Hotline call to QSEs: Typical Script: “This is <state your name>, ERCOT is in the process of transferring operations from the primary control center to the backup control center due to <define situation>. Further information will be forthcoming as necessary. Until further notice, all phone calls to ERCOT should be directed to (512) 225-7100. All QSEs are to follow their base power schedules and hold the last good interval. QSE XXX, go on constant frequency to control the frequency. QSE are to maintain their voltage profiles. Are there any questions?” Hotline call to TOs: Typical Script: “This is <state your name>, ERCOT is in the process of transferring operations from the primary control center to the backup control center due to <define situation>. Further information will be forthcoming as necessary. Until further notice, all phone calls to ERCOT should be directed to (512) 225-7100. Until further notice, please notify ERCOT when thermal limits reach 85% of the static rating. Zonal transfers and the West to North stability limits are to be reported when power flows reach 85% of their respective limits. Transmission voltages are to be reported when approaching 0.95 or 1.05 per unit. Are there any questions?” |
| --- | --- |
| 5 | The Shift Supervisor will notify the following: - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations - Engineering Support - NERC - Call out shift personnel to staff the backup site, including a Shift Supervisor, unless Primary Control Center shift will be relocating from the primary control center to the Backup Control Center. These phone numbers have been programmed into the control room cell phone. |
| 6 | Monitor critical transmission and generation facilities, the list is provided in the procedure manual under “Critical Assets”. |
| 7 | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |