Power Operations Bulletin # 367

ERCOT has revised the Transmission & Security Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### 2.1.2 Real Time Contingency Analysis (RTCA) Constraint Validation |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 20 minutes. |
| 3 | If RTCA has not run within 20 minutes, refer to “RTCA Call Out Procedure” in section 2.1.3. |
| 4 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist, - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are located in the daily Outage Notes. |
| 4a | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or - 4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take the DIRECT appropriate voltage control action. |
| 5 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 6 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Addendum 1 for guidance. |
| 7 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 8 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 9 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 10 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Take additional manual actions as necessary to resolve the contingency overload within 30 minutes. As time permits, notify the on-call Operations Support Engineer. If the system operator determines that the Pre-contingency value or system topology is incorrect, OR if a SPS, RAP, PCAP, TOAP, or MP exists, step 10 may be omitted. |
| 11 | If congestion management techniques fail to resolve congestion and the transmission system is beyond first contingency criteria, ISSUE an Alert per section 2.5.3. |
| 12 | Periodically check the Base Case violations display for Thermal overloads. |
| 13 | If a Thermal overload exists in real time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 14 | Periodically check the “Contingency Solution Results” display. If there are more than five (5) unsolved contingencies, run the State Estimator again. If more than five (5) remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. - Contingencies that are known to remain unsolved, or have been reported before, should not be included in the five (5) mentioned unsolved contingencies. |

| ### 2.2.3 Zonal (CSC) Congestion Management |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTES: | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. Potential IROLs are defined in the day-ahead analyses or when changes in system conditions warrant further evaluation. If a CSC has been marked as an IROL on the “Transmission Limits” sheet, ensure the limit is honored. If the limit is violated, take all possible actions to get below the limit in 30 minutes or less. The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary, to ensure system security. Constraint: A contingency and limiting Transmission Element pair that is an anticipated or actual security violation or overload of a transmission element, based on actual network topology. - Utilize Zonal Techniques to resolve flow limit violations on any CSC/CRE constraint. - Utilize Local Congestion Techniques to resolve flow limit violations on any non CSE/CRE constraint. A current list of CSC/CRE DATA is posted on the following ERCOT website: http://mospublic.ercot.com/ercot/jsp/csc_cre.jsp |
| 1 | When a CSC or CRE approaches or exceeds its limit on the “Transmission Limits to be Monitored” daily report, EMPLOY Zonal Techniques. - As the CSC/CRE approaches its limit, the system operator may use his/her discretion when to implement congestion management, either before or at the time the limit is exceeded, depending on system conditions. |
| 2 | When RTCA shows a post contingency overload on a posted ERCOT CSC/CRE, AND the CSC/CRE has not exceeded its’ limit on the “Transmission Limits to be Monitored” daily report, AND RTCA has solved within the last 10 minutes, then RTCA results should be used as a basis for managing zonal congestion. |
| 3 | If Zonal Techniques fail to control the flow within NERC requirements, utilize Local Congestion Management Techniques. - Use the MIS to post that local techniques are being used to control CSC congestion. Typical Script: “Zonal congestion management techniques have been unsuccessful in controlling the “<zone – zone>” CSC congestion. Local techniques will be utilized.” |
| 4 | If OOME becomes necessary, units that have their HSL and LSL set to the same value cannot respond to market deployments and may be deployed to 0 output. |
| 5 | IF RTCA values are being used to control a CSC due to a significant unexpected change in system conditions which is likely to last for an extended period of time, - NOTIFY Operations Support to determine if a new limit should be calculated. - Use the MIS to post that ERCOT is controlling to RTCA values to control CSC congestion. As time permits. Typical Script: “ERCOT is controlling to RTCA results to control the “<zone – zone>” CSC congestion.” |
| 6 | IF a new Zonal limit is calculated by Operations Support, post it on the MIS and ENS, AND control to the new limit. |
| NOTE: | Zonal limits may change due to an outage cancellation, extension of an outage, or the early completion of an outage. |

| ### 2.2.7 SPS Intervention |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Note: | The ERCOT Transmission & Security operator will re-dispatch generation to prevent any known SPS from operating. Generation will not be re-dispatched to prevent post contingency overloads in cases which an SPS will automatically relieve the overload. |
| 1 | If the system operator receives a call from a TSP or observes that a SPS is about to operate, then congestion management techniques should be employed in an attempt to prevent its’ activation. |

| ### 2.5.5 Notification of Condition Termination |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Alert, Advisory, or Emergency Notice will constitute cancellation of the previous notification. |
| 1 | When the situation requiring the notification is relieved, NOTIFY Market Participants and Transmission Operators that the condition has been terminated. OCNs do not require “termination” notification. - Place termination time in ENS - Make Notices invalid in MIS - Initiate a hotline call to all Transmission Operators - Notify the Frequency desk to initiate a hotline call to all QSEs - Print Hotline log and save in daily log as time permits |

| ### 2.5.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for conservation is enacted TO’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue if necessary until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |

| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MWs, OR - ERCOT has deployed over 760MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| --- | --- |
| 1b | Using the hotline, notify all TOs to implement EECP STEP 1. - Print the Hotline log Typical script: “ERCOT has implemented EECP STEP 1.” |
| 1c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor, as time permits. |
| 1d | Ensure the following is complete: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 1e | Implement Section 2.5.8 of this procedure for emergency energy across the South DC-Ties. |

| 2a | In addition to measures associated with STEP 1; Implement EECP Step 2 IF, - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| --- | --- |
| 2b | In conjunction with the ERCOT Frequency Control Desk Operator, implement EECP STEP 2. Using the hotline, notify all TOs to implement EECP STEP 2. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor, as time permits Typical script: “ERCOT has implemented EECP STEP 2; - LaaRs have been deployed - Within the time frame of the emergency, TOs that have the ability are to implement Block Load Transfers and transfer load from the ERCOT control area to Non-ERCOT control areas - If local operating conditions permit, TOs are to reduce customer loads by using distribution voltage reduction measures - Report back to ERCOT when these actions have been initiated and/or completed |
| 2c | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures that have been taken. |
| 2d | Unless a media appeal is already in effect, issue an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) Notify TO’s that a media appeal for conservation is in effect via Hotline. |

| 3a | In addition to measures associated with STEP 1 & 2; Implement EECP Step 3 IF: LAARs have been deployed AND EILS has been procured, AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| --- | --- |
| NOTE: | There are two separate blocks of EILS: The first is called EILS Business Hours: Business hours are defined as HE 0900- HE 2000 on Business Days Monday through Friday not to include Holidays. The second is called EILS Non-Business Hours: Non- Business Hours are classified as any hour not defined as Business Hours. When a deployment of EILS is implemented and the event is still in effect when one Time Period (either Business Hours or Non-Business Hours) ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. QSEs representing EILS Resources that are obligated in the new Time Period shall not deploy the newly obligated EILS Resources unless instructed to do so by ERCOT. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. When issuing a VDI for EILS specify Non- Business Hours or Business Hours in the Instruction Section of the VDI. |
| 3b | Using the hotline, notify all TOs to implement EECP STEP 3. When TOs have answered the Hotline, print the Hotline log and forward it to the Shift Supervisor, as time permits. Typical script: “ERCOT has implemented EECP Step 3. EILS are being deployed |

| 4a | In addition to measures associated with STEP 1, 2 & 3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| --- | --- |
| NOTE: | Firm load is to be shed in 100 MW blocks. TOs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of EECP. |
| 4b | Using the hotline, notify all TOs to implement EECP STEP 4. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT has implemented EECP Step 4. ERCOT is instructing all Transmission Operators to shed their share of <amount> MWs. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load shed.” |
| 4c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor, as time permits. |
| 4d | Inform the Frequency Control Desk Operator that notifications have been completed to the Transmission Operators to shed firm load. |
| 4e | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures have been taken where possible - Load shed instructions have been received and enacted. |

| ### 2.5.7 Restore EECP Steps |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP Restoration. EECP STEPS in this procedure are to be implemented in concert with the Frequency Control Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| 4 | Begin restoring firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MWs |
| 4a | Using the hotline, notify all TOs of firm load restoration. - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor, as time permits. Typical Script: “ERCOT is instructing all Transmission Operators to now restore their share of <amount> MWs leaving <amount> MWs still off. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load restored.” |
| 4b | Ensure the following: - “ERCOT is restoring firm load” is posted on the Emergency Notification System (ENS) short version – 32 characters - “ERCOT is restoring firm load” is posted on the Market Information System (MIS) |
| 4c | Maintain Adjusted Responsive Reserve supplied from generation equal to 1150 MWs while restoring firm load. |
| 4d | Ensure that the Frequency Control Desk Operator notifies the QSEs that firm load is being restored. |

| 4e | Move from EECP STEP 4 to STEP 3 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored |
| --- | --- |
| 4f | Using the hotline, notify all TOs of the reduction from EECP Step 4 to Step 3: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “ERCOT is moving from EECP Step 4 to Step 3.” |
| 4g | Ensure the following: - EECP Step 4 to Step 3 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 4 to Step 3 is posted on the Market Information System (MIS) |
| 4h | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |
| 4i | When directed by the Frequency Control Desk Operator, use the hotline and notify the TOs that LaaRs are being restored. |
| 4j | Resend distribution voltage reductions measures as appropriate. |

| 3 | Move from EECP STEP 3 to STEP 2 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| --- | --- |
| 3a | Using the hotline, notify all TOs of the reduction from EECP Step 3 to Step 2: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor as time permits. Typical script: “ERCOT is moving from EECP Step 3 to Step 2.” |
| 3b | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |
| 3c | Appeal through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisors procedures) |
| 3d | Ensure Southwest Power Pool Security Coordinator is updated on ERCOT’s status. |

| 2a | Move from EECP Step 2 to Step 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MWs, AND - All LaaRs have been restored, or replaced with generation. |
| --- | --- |
| 2b | Using the hotline, notify all TOs of the reduction from EECP Step 2 to Step 1: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor as time permits. Typical script: “ERCOT is moving from EECP Step 2 to Step 1, All EILS are being recalled..” |
| 2c | Ensure the following steps are complete: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters EECP Step 2 to Step 1 is posted on the Market Information System (MIS |
| 2d | If Block Load Transfers have been executed, restore them as system conditions permit. Typical Script: “TOs who have transferred load to Non-ERCOT control areas may restore such load as local conditions permit. Keep ERCOT advised on the progress and completion this task.” |
| 2e | Instruct the Frequency Control Desk to notify QSEs that BLTs are being restored. |
| 2f | Recall EILS. Maintain a minimum of 2300 MWs of Adjusted Responsive Reserve.. Move from EECP Step 1 to Termination when: - All EILS resources have been recalled, AND - All uncommitted units secured in EECP STEP 1 can be release to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 1a | Move from EECP Step 1 to Termination when: - EILS resources have been recalled. AND - All uncommitted units secured in EECP STEP 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND Sufficient Regulation Service exist to control to 60 Hz. |
| 1b | Using the hotline, notify all TOs of the reduction from EECP Step 1 to termination: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor, as time permits. Typical script: “ERCOT is terminating EECP. An Alert still remains in effect.” |

| ### 2.5.8 Scheduling Emergency Power across the South DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| ###### NOTE: | ###### The South DC Ties include Eagle Pass (DC_S), Railroad (DC_R), and the Laredo variable frequency transformer (DC_L). |
| NOTE: | Declare the appropriate emergency notification when necessary. |
| 1 | ERCOT will contact AEP TDSP to verify if power is available for transfer on the South DC Ties. If power is available for transfer, determine the MW amount, how soon it would be available, and duration of the schedule. |
| 2 | ERCOT must give AEP QSE a VDI. Forward to Shift Supervisor as time permits. |
| 3 | Approximately 20 minutes before the schedule begins, ERCOT will contact AEP TDSP to verify that AEP will start the emergency schedule across the South DC Ties. ERCOT should verify the start time, MW level, and duration of the emergency schedule. |
| 4 | Approximately 20 minutes before the schedule ends, ERCOT will contact AEP TDSP to verify the stop time of the emergency schedule across the South DC Ties. |

| ### 2.5.9 Block Load Transfer |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The necessary Market Participant agreements, metering, and ERCOT settlement systems are to be in place prior to implementation of any BLT. |
| NOTE: | Conditions for BLT Implementation: An Emergency Notice must be posted on the ENS and MIS for any BLT. From Non-ERCOT Control Area into ERCOT - When Non-ERCOT Control Area experiences certain transmission contingencies or short supply conditions. - Under specific Dispatch Instruction from ERCOT. From ERCOT to Non-ERCOT Control Area - Under Alert or EECP - Under specific Dispatch Instruction from ERCOT and permission of the affected Non-ERCOT Control Area. |
| 1 | If an ERCOT TO becomes involved in a Block Load Transfer (BLT) from a Non-ERCOT Control Area into ERCOT, execute the following: - Verify that the load being picked-up by ERCOT is a registered Load Serving Entity (LSE) with ERCOT (treated as a load in the ERCOT settlement system). - Verify LSE/QSE affiliation has been executed. - TDSP/TO associated with the BLT Point is responsible for the creation and maintenance of ESI ID. - The QSE of the LSE assigned to the ESI ID associated with the BLT Point will include that load in its balanced schedules. - Determine with the TO an estimated time it will take to transfer the load. - Determine the amount of load being transferred into ERCOT. - Consult with the Operation Engineering Support to ensure system security has been addressed. - Notify the Manager, System Operations that a BLT has been initiated. - To enhance the communications ERCOT may request that a conference call be implemented at the appropriate time between ERCOT, the TO and the Non-ERCOT Control Area. - If the TO requests a VDI, issue a VDI to the TO. For verification information, refer to the Shift Supervisors procedure book (Registered BLTs tab) for a current list of registered BLTs. |
| 2 | Congestion management issues that arise from switching variations due to BLTs will be handled per ERCOT’s congestion management procedures. |
| 3 | If an ERCOT TO becomes involved in a Block Load Transfer (BLT) from ERCOT to a Non-ERCOT Control Area, execute the following: - Verify that the QSE of the Resource associated with the BLT includes that Resource in its Resource Plan (treated as a Resource in the ERCOT settlement system and will be established as a pseudo generation facility). - Verify the creation of an ERCOT registered Resource Entity. - Verify Resource Entity/QSE affiliation has been executed. - Verify a BLT Registration form has been completed. - Verify metering design documentation has been provided to ERCOT. - Determine the amount of load being transferred out of ERCOT. - Notify the Manager, System Operations that a BLT has been initiated. - To enhance the communications ERCOT may request that a conference call be implemented at the appropriate time between ERCOT, the TO and the Non-ERCOT Control Area. For verification information, refer to the Shift Supervisors procedure book (Registered BLTs tab) for a current list of registered BLTs. |
| 4 | Once it has been determined which QSE will supply the power, issue a VDI to the requesting QSE (Any energy delivered under such a Dispatch Instruction shall be treated as an OOME Dispatch Instruction to the QSE). |
| 5 | BLTs to or from ERCOT may be curtailed or terminated in order to maintain the reliability of the supporting system. Discuss with TO the process and time it will take to separate the connection if a reliability issue arises. |

| ### 2.6.6 Monthly Testing of Satellite Phone System |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Purpose: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| Note: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 2 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Attachment B of the ERCOT Satellite Phone User Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 3 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 4 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form (SEE Appendix 10). An electronic copy of this form is located in P:\ SYSTEM OPERATIONS ”Satellite Bridge Testing forms” folder. |
| 5 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is complete. |
| 6 | Log the test date and results in the ERCOT Operations Log. |
| NOTE: | Send an e-mail to “1 ERCOT Training Department” for any Satellite phone problems during the test. |