## Power Operations Bulletin # 380

ERCOT has revised the Frequency Control Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### 2.6.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue if necessary until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |

| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MWs, OR - ERCOT has deployed over 760MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| --- | --- |
| 1b | Using the hotline, notify all QSEs to implement EECP STEP 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 1, QSEs are to enact the following”: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - Start and load all available RMR units to full capacity within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. |
| 1c | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |
| 1d | Ensure the following: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 1e | Ensure all available Non-Spin has been deployed. |
| 1f | Notify the ERCOT DC-Tie Desk of the EECP status. |
| 1g | VERIFY and log the following as appropriate: - All RMR units are at, or being loaded to, full capacity - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources - Available DC Tie capacity not being used by the market has been applied to the system. (Generally, this will not affect export schedules out of the ERCOT Control Area.) |

| 2a | In addition to measures associated with STEP 1 Implement EECP Step 2 IF: - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LAAR) |
| --- | --- |
| 2b | Using the hotline, notify all QSEs to implement EECP STEP 2. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP STEP 2; - QSEs are to deploy all Loads acting as a Resource (LAARs) bid to supply Responsive Reserves Service within ten (10) minutes. - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed,” |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TO via the Hotline that LAARs have been deployed. |
| 2d | Ensure printed Hotline log has date and time information and forward it to the Shift Supervisor. |
| 2e | Ensure the following: - EECP Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 is posted on the Market Information System (MIS) |
| 2f | Notify the DC-Tie-Desk of change EECP status. |
| 2g | Unless a media appeal is already in effect, ask the Shift Supervisor about the issuance of an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) |
| 2h | Dispatch any unutilized remaining capacity. |
| 2i | VERIFY and log the following as appropriate: - RMR units are at, or being loaded to full capacity. - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources. - LAARs have been deployed. |

| NOTE: | EILS Resources have 10 min. to comply with this instruction. If conditions develop that require implementing EECP step 4, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| --- | --- |
| 3a | In addition to measures associated with STEP 1 & 2; imPLEMENT eecp sTEP 3 IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. |
| 3b | Using the hotline, notify all QSEs to implement EECP STEP 3. When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 3. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources at (time) until further notice. All QSEs confirm that their generation resources are at maximum output.” |

| 4a | In addition to measures associated with STEP 1 & 2,3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| --- | --- |
| 4b | Ensure that the Transmission & Security Desk Operator has completed notifications to the Transmission Operators to shed firm load before proceeding to Step 4c. |
| 4c | Using the hotline, notify all QSEs to implement EECP STEP 4. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is [operator’s first and last name]. ERCOT has implemented EECP Step 4. Transmission Operators have been instructed to shed <MW Amount> of firm load. All QSEs confirm that their generation resources are at maximum output.” |
| 4d | Ensure the printed Hotline log has date and time information and forward it to the Shift Supervisor. |
| 4e | Notify the ERCOT DC-Tie Desk of change in EECP status. |
| 4f | In conjunction with the Transmission & Security Desk Operator, - Ensure EECP Step 4 is posted on the Emergency Notification System (ENS) short version – 32 characters - Ensure EECP Step 4 is posted on the Market Information System (MIS) |
| 4g | VERIFY the following: - All Generation Resources are at full capacity - All RMR units are at full capacity - Available Non-Spin has been deployed in the period of the emergency. - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended. - Available DC Tie capacity not being used by the market has been applied to the system - SPP Security Coordinator has been updated on ERCOT’s status - All LAARs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

| ### 2.6.7 Restore EECP Steps |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP Restoration. Numbering of procedure steps is reversed to coincide with EECP Steps. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LAARs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| 4a | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. |
| 4b | Move from EECP STEP 4 to STEP 3 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND All firm load has been restored. |
| 4c | Using the hotline, notify all QSEs of the reduction from EECP Step 4 to Step 3: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is moving from EECP Step 4 to Step 3.” |
| 4d | Ensure the following: - EECP Step 4 to Step 3 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 4 to Step 3 is posted on the Market Information System (MIS) |
| 4e | Notify the ERCOT DC-Tie Desk of change in EECP status. |
| 4f | Begin recalling LAARs as sufficient capacity from generation becomes available. Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LAARs are being restored. |
| 4g | Instruct the Transmission & Security Desk Operator to notify the TOs that LAARs are being restored. |

| 3a | Move from EECP STEP 3 to STEP 2 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LAARs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |
| --- | --- |
| 3b | Using the hotline, notify all QSEs of the reduction from EECP Step 3 to Step 2: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is moving from EECP Step 3 to Step 2.” |
| 3c | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |
| 3d | Appeals through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisor desk procedure) |

| 2a | Move from EECP Step 2 to Step 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MWs AND - All LAARs have been restored or replaced with generation. |
| --- | --- |
| 2b | Using the hotline, notify all QSEs of the reduction from EECP Step 2 to Step 1: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is moving from EECP Step 2 to Step 1.” |
| 2c | Ensure the following steps are complete: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 to Step 1 is posted on the Market Information System (MIS) |
| 2d | Recall EILS. Maintain a minimum of 2300 MWs of Adjusted Responsive Reserve. |
| 2e | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS is being recalled. |
| 2f | Notify the ERCOT DC-Tie Desk of change in EECP status. |

| 1a | Move from EECP Step 1 to Termination when: - EILS resources have been recalled. AND - All uncommitted units secured in EECP STEP 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |
| --- | --- |
| 1b | Using the hotline, notify all QSEs of the reduction from EECP Step 1 to termination: - Print the Hotline log - Ensure the log has the date and time noted and forward it to the Shift Supervisor. Typical script: “This is [operator’s first and last name]. ERCOT is terminating EECP. An Alert still remains in effect.” |
| 1c | Ensure the following: - EECP Step 1 termination is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 termination is posted on the Market Information System (MIS |
| 1d | Notify the ERCOT DC-Tie Desk of change in EECP status. |

| ### Import and Export Limits for the Railroad DC Tie and Laredo VFT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Daily import and export limits for the Railroad DC Tie and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored Sheet”. |
| 1 | After midnight, verify that the daily import and export limits have been updated in RTMONI and are displayed correctly on the ERCOT website at: http://mospublic.ercot.com/ercot/jsp/frequency_control.jsp |
| 2 | Verify the limits with the DC-Tie Operator. |

| ### 2.7.3 Approve NERC Tags for Railroad DC Tie and Laredo VFT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | Currently the Eagle Pass DC Tie (DC_S) is not available for commercial operation. Only emergency schedules can flow across the Eagle Pass tie. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-tags. |
| PURPOSE: | A NERC Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments. |
| 1 | When a new or updated tag is received in the OATI WebTrans system: - Determine if the following information is correct on the NERC E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the NERC E-Tag, deny the tag, otherwise go to Step 1.2. - Determine if one or more NERC E-Tags being submitted will cause the DC Tie to exceed the schedule MW limit for the tie. - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the schedule MW limit for the tie. - Curtail the NERC E-Tag(s) to 0 (zero) based on Last-in-first-out (LIFO) until under the schedule MW limit for the tie. - Determine if the tag passed or failed validation. - If the tag passes validation, go to Step 2. - If the tag fails validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag fails validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve a NERC E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the tag approval timeline, the tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the tag to the schedule: - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E-Tag. - If the tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” bow will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

| ### 2.7.4 Adjustment of DC Ties (includes all commercial DC-Ties) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | When an adjustment alarm is received in WebTrans: - Determine if the tag passed or failed validation. - If the tag adjustment passed validation, approve the adjustment. - If the tag adjustment failed validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag adjustment failed validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor |
| 2: | Periodically refresh the QSE Summary display during the tag adjustment approval window to determine if a QSE has changed an MOI schedule that is now making the NERC E-Tag fail validation. - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the NERC E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E- Tag. - If the tag equals the MOI schedule, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |
| NOTE | Tag adjustments must be in an “Approved” or “Implemented” status to be calculated Into the Net Scheduled Interchange (NSI) |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by NERC E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

| ### 2.7.5 Curtailment of East and North DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | When a curtailment alarm is received in WebTrans, - Approve the tag curtailment. WebTrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| 2 | If a QSE or SPP requests a tag be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |
| NOTE | Tag curtailments must be in an “Approved” or “Implemented” status to be calculated Into the Net Scheduled Interchange (NSI) |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by NERC E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

| ### Curtailment for Road DC Tie and Laredo VFT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE: | Scheduling limits for the ROAD DC Tie and Laredo VFT can change due to changes in generation, transmission configuration, weather, and other system conditions. After receiving the import/export limits for next day, it may be necessary to curtail schedules. |
| 1 | If a scheduling limit changes that causes the DC Tie(s) to be overscheduled, review the NERC E-Tags and curtail to 0 (zero) based on Last-in-First-Out (LIFO) until under the scheduling limit of the DC tie. |
| 2 | Coordinate with the DC Tie Operator to ensure that CFE approves the curtailment. |
| 3 | If a QSE requests a tag to be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |

| ### 2.7.7 Managing and Documenting Daily Inadvertent for North and East DC-Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties - Contact AEP Corpus Christi TO for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| NOTE: | When no schedules are flowing across the North DC Tie AEP Ohio TO may execute a program that will automatically flow 25MW out of ERCOT and into SPP across the North DC Tie. OR If there are schedules flowing across the North DC Tie and the net scheduled value is less than 25 MW, AEP Ohio TO will control the tie to approximately 25MW in the direction of the schedule flow to keep inadvertent to a minimum. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5. | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

| ### 2.7.8 Managing and Documenting Daily Inadvertent for the Eagle Pass, Laredo and Railroad DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ROAD_DC, or LAR_VFT) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). The Eagle Pass DC Tie is not available for commercial operation at this time. The normal scheduled and actual values should be zero (0) However if emergency energy flowed actual values will exist. |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TSP for the North and East DC Ties - Contact AEP Corpus Christi TSP for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - Give the integrated actual value for the Eagle Pass, Laredo and Railroad DC Ties indicated on the “Tie Data” display in WebTrans. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. No further action is required. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values: - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, instruct the DC Tie Operator to change their value to match ERCOT’s value. WebTrans Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the South DC-Ties and email to the following: - CFE DC-Tie Inadvertent |

| ### 2.7.9 Managing Inadvertent Payback (includes all DC Ties) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Payback will only be planned when there is room on the DC Tie(s). Power schedules of market participants will supersede any inadvertent payback plan. Payback plans are implemented by the DC Tie Operator. They will bias the DC Tie(s) and create inadvertent in the opposite direction. This will reduce the inadvertent values. |
| NOTE: | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback plan information from the Manager of System Operations. |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties - Contact AEP Corpus Christi TO for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Prior to the start of the Payback plan, call the appropriate DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback plan. If payback is planned across the VFT, verify the transmission path (230kV or 138kV). |
| 2 | Periodically check the WebTrans system to ensure that the inadvertent values are decreasing. If they are not decreasing or are increasing, call the DC Tie Operator to determine the reason. WebTrans Reference Display: Daily Inadvertent |
| 3 | Prior to the Payback plan stopping, call the appropriate DC Tie Operator and confirm the agreed upon stop time. |

| ### 2.7.10 Emergency Energy across the South DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ERCOT must declare an emergency and make the proper posting/hotline call when receiving emergency energy. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| NOTE: | Transmission Emergencies will be coordinated with the ERCOT Transmission & Security Desk. |
| 1 | ERCOT and/or CFE will contact the DC-Tie Operator (AEP TO in Corpus) to verify if power is available for transfer on any of the South DC-Ties. If energy is available for transfer, determine the DC-Tie(s), MW amount, time and duration (if possible). |
| 2 | For emergency energy to flow across the Railroad DC-Tie or Laredo VFT, notify AEP (SQ4) QSE with the information listed in step 1 to enter the E-Tag. |
| 3 | Issue AEP QSE (Generation Dispatchers) a VDI for the emergency energy. Forward to Shift Supervisor (fax) as time permits. |
| 4 | Emergency energy across the Eagle Pass DC-Tie does not need an E-Tag submitted. Issue AEP QSE (Generation Dispatchers) a VDI and coordinate with the DC-Tie Operator. |

| ### 2.7.11 EEA 1 Schedule across the SPP DC Ties for EEA 1 (EECP 1) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Notify the SPP Reliability Coordinator of ERCOT’s EEA 1 status. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA 1. We will contact the Tariff desk to inquire about the availability of transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2, proceed to Section 2.7.7 If there is transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the transmission service available. Thank you.” |
| NOTE: | SPP will contact PSEs with unscheduled reservations and notify them of ERCOT’s EEA 1 status. PSEs may choose to use their reservation to schedule into ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers): Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. - If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-tag(s) and proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify the DC Tie Operator of ERCOT’s EEA status. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag (s) for an EEA 1 schedule. |

| ### 2.7.12 Emergency Energy Request across the SPP DC Ties for EEA 2 or 3 (EECP 2 - 4) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE: | If ERCOT goes directly to an EEA 2 or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below. |
| 1 | Notify the SPP Reliability Coordinator: Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will contact the Tariff desk to inquire about the availability of emergency transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the emergency transmission service available. Thank you.” |
| NOTE: | ERCOT must have the RCIS updated with the EEA 2/3 status before granting emergency transmission service. |
| NOTE: | SPP will curtail all non-firm transmission service schedules going out of ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-tag(s). Proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status: Typical Script: “This is [operator’s first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| NOTE: | Keep SPP informed of ERCOT’s status. |

| ### 2.7.13 Backing out of EEA’s and Termination |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | When moving EEA status: Notify the SPP Reliability Coordinator of ERCOT’s status. Typical script: “This is [operator’s first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify the Tariff desk, please transfer me. Thank you.” |
| 2 | Notify the SPP Tariff desk of ERCOT’s EEA status. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify AEP. Thank you.” |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status. Typical Script: “This is [operator’s first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| NOTE: | Repeat above steps with the notifications until ERCOT’s status is EEA 0 (zero). |

| ### 2.7.14 Fast Start Emergency Schedules to Southwest Power Pool (SPP) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Every effort should be made to render assistance during emergency conditions. SPP will notify ERCOT that emergency assistance is needed. |
| 1 | VERIFY that providing emergency assistance to SPP will not put ERCOT in an insecure state, or worsen an existing insecure state. |
| NOTE: | SPP will contact the DC Tie Operator and arrange to maximize the DC tie output into SPP. It is not necessary to confirm that an emergency condition has been posted in the RCIS. SPP may need to act before the RCIS is updated. |
| 2 | Notify the Operating Period Desk to adjust the Offset to minimize the use of Regulation. |
| 3 | When possible: - Contact AEP QSE and instruct them to create and submit a NERC tag for the emergency assistance (this can be done after-the-fact but within an hour of the event). - Issue a VDI to AEP QSE for the emergency assistance. |