## Power Operations Bulletin # 387

ERCOT has revised the Frequency Control Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### 2.1.1 Control Generation to Ensure Load Is Covered |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Monitor the current ERCOT System Load and Short Term Load Forecast. Reference Displays: Generation Area Status Short-Term Load Forecast MAI (Market Analysis Interface) |
| 2 | Determine that the current ERCOT System generation capacity is sufficient to meet the Short-Term Load Forecast requirements. Reference Displays: Generation Area Status MAI (Market Analysis Interface) |
| 2a | Compare the current generation and load with the planned capacity values from resource plan at least every other hour. Reference Displays: Generation Area Status Daily Operation Plan – Resource Plan MAI (Market Analysis Interface) |
| 2b | If real-time generation is approaching planned capacity a possible shortage is developing. Discuss situation with Operating Period Desk and Shift Supervisor, and increase monitoring of reserves. Reference Displays: Generation Reserve Status – Available Details Real Time Balancing Market – Balance Bid Tab Real Time Balancing Market – QSE Tab MAI (Market Analysis Interface) |
| 3 | If a shortage is developing in the next hour, consider OOMC or deploying of Non-Spinning Reserve Service. Consult with the Operating Period Desk regarding hour-ahead study results. |
| 4 | If OOMC is decided upon, request the Transmission & Security Desk perform the actual instruction. If NSRS is decided upon, request the Operating Period Desk perform the actual instruction. |
| 5 | MONITOR additional available generation capacity and available DC tie capacity. Evaluate amount of additional capacity available in a short time frame using telephone communications to QSEs as appropriate. Reference Displays: Generation Area Status Generation Reserve Status Generation Tie-Line Status |
| 6 | Monitor Responsive Reserves on the QSE Reserve Status Display. If Adjusted Responsive Reserve plus LaaRs is correctly calculated, and is below 2300 MW, - notify the Shift Supervisor - implement EECP - log in the Operator’s Log any decision to declare an EECP. |
| 7 | Monitor Ancillary Service Obligations If a QSE is not meeting its Ancillary Services obligations as shown on the QSE Reserve Status Display, - contact the QSE to correct the deficiency - notify the Shift Supervisor of the QSE’s response - log the activities performed in connection with this step |

| ### 2.1.2 Verbal Dispatch Instructions (VDI) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | ISSUE a VDI to QSE(s) to give a directive. |
| NOTE: | VDIs should not re-iterate an instruction given via XML. |
| NOTE: | Whenever a VDI is issued, request the QSE to repeat back the instructions. IF the QSE Hotline is used to issue a VDI, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the instructions and direct a repeat back again. Continue until an acceptable repeat back is received. |
| 1 | As time permits, complete the VDI form (Appendix 3). The following are required fields on all VDIs: - VDI # - EXAMPLE: For the 4th VDI issued by the Frequency Control Desk on July 22, 2005 the number would appear as “F-072205-4” - Operating Day - ERCOT System Operator - Receiving Entity - Receiving Entity’s Operator - Time & Date - Instruction - Reason for Instructions - Intervals - Repeated Instruction back - ERCOT Operator’s signature Blank fields are to have N/A entered. |
| 2 | LOG in the Operator’s Log the VDI information and information relevant to the decision for issuing the VDI. |
| 3 | Forward the VDI form to the Shift Supervisor, as time permits. |

| ### 2.1.3 VDI for Hold Last Interval |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| ###### NOTE: | An Alert must be issued if two (2) consecutive Real-Time Balancing Intervals are held as per procedure 2.6.3 step 1. |
| 1 | If market control mechanisms have failed, or ERCOT has issued erroneous instructions THEN, using the hotline, issue an instruction: - When QSEs have answered the Hotline, print Hotline Log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing VDI # ______. Hold the [interval ending time] interval Balancing Energy deployment until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | As time permits complete the VDI form (Appendix 3), using these instructions: - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows – write in “Hold interval ending <time>, resume with interval <time> - Instruction repeated back ALL fields are to have either pertinent data or N/A entered. Leave NO field(s) blank. |
| 3 | A held interval message must be posted on the MIS and ENS: Typical posting: Real-time balancing deployments were held for IE XX:XX. |
| 4 | LOG in the Operator’s Log the VDI information and reason(s) why interval was held. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward, along with VDI to the Shift Supervisor, as time permits. |

| ### 2.1.7 Replacing Responsive Reserve through a Bilateral Trade |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | A QSE has the option to reduce their base power schedule and replace the difference from the balancing market. This will allow the QSE to back down their generation so they can provide their Ancillary Service obligation. (REF. PRR 404) |
| NOTE: | When a resource (either LaaR or generation) that is supplying RRS becomes unavailable to a QSE (QSE A) and needs to be replaced through a Bilateral Trade with another QSE (QSE B), then QSE A is expected to inform ERCOT. |
| 1 | Obtain the following information from QSE A: - Intervals affected - Name of QSE with whom the bilateral trade was made |
| 2 | IF the resource that became unavailable was a LaaR, then ENSURE QSE B maintains an amount of Responsive Reserve Service equal to their own obligations PLUS the amount of the bilateral agreement with QSE A for the affected intervals. |
| 3 | If the QSEs response is not satisfactory, notify the Shift Supervisor so a determination of protocol violation can be made. LOG in the Operator’s Log the conversation, including the information provided. |
| 4 | Email the information RRSList@Ercot.com. |

| ### 2.2.1 QSE Telephone Hotline Test |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline. |
| 2 | Check with the Shift Supervisor and determine the ERCOT current threatcon level. |
| NOTE | In the event of a failure of the Confertel software, the most recent printout of the hotline log may be used as a checklist to perform a manual roll call of QSEs. |
| NOTE | Insure all “Lost Souls” are cleared prior to the hotline call. |
| 3 | Using the hotline, notify all QSEs of the purpose of the call. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is conducting the weekly QSE hotline test. We are currently at threatcon level [threatcon level]. The following notices are currently in effect: - List OCNs, Advisories, Alerts and/or Emergency Notices in effect. - State “None” if none in effect. This ends this test of the ERCOT Hotline. That is all.” |
| 4 | Notify the Shift Supervisor of any QSE that did not respond to the Hotline test. The Shift Supervisor and/or Help Desk may notify the telecommunications department for repairs. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.2.2 Site Failover Hotline Message |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Using the hotline if available notify all QSEs before the scheduled time for a planned site failover (preferably five (5) to 30 minutes). The following message should be communicated. The variable information is in brackets. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. At [time], ERCOT will perform a planned site failover of its Energy & Market Management Systems from [Taylor] to [Austin]. During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about five minutes. All systems should reestablish communications automatically.” |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.5.1 Frequency Control Operating Procedure |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| 1 | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or - “Last AGC Cycle” time on Generation Area Status display is not updating or AGC operation adversely impacts the reliability of the Interconnection Place a large QSE (that has regulation reserve) on constant frequency. |
| 2 | Using the Hotline, notify all QSEs that ERCOT is having computer issues and is putting a QSE on constant frequency. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is currently having computer issues and has put a QSE on constant frequency until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 3 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| NOTE: | If the QSE that is put on constant frequency is having trouble keeping up, issue fleet VDI’s to other QSE’s to help out or put a different QSE on constant frequency. Remember to take the first QSE off constant frequency. |
| 5 | When frequency control is functioning, remove the QSE from constant frequency. |
| 6 | Notify all QSE’s by Hotline that ERCOT is back on control. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is back to normal operations. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 7 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 8 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 9 | At the operator’s discretion, turn off SCE feedback for Regulation Providers with Participation Factors less than 1% (<0.01). |
| 10 | Monitor QSE generation and SCE: - Remove a QSE’s SCE feedback if they have a large SCE and their generation is not moving in the proper direction or rate to correct their SCE. Reference Display Responsive, Regulation, and SCE Regulation |
| 11 | NEVER (unless directed by the Control Engineer or designee): - Modify “Total (SCE-responsive) Feedback Gain” (should be altered by the Control Engineer) - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) Reference Displays: Responsive, Regulation, and SCE – Details |
| 12 | LOG in the Operator’s Log frequency deviations of greater than or equal to 0.10 Hz. Record the following: - Possible reasons if known. (SCE, Large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped. - Approximate MW that was on the unit when the unit tripped. - Approximate ERCOT load. |

| ### 2.5.4 Operator Instructions for High Frequency |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
|  | The following steps are to be taken in the event of High system frequency of unknown cause. If the cause of High system frequency is known and system response or other actions are expected to correct it, then the following steps are optional. |
| NOTE: | The Frequency Control Desk Operator may consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. |
|  | Frequency above 60.05 and continuing to climb or over 60.05 > five minutes. |
| 1 | If regulation down service remains and is deploying: - Call QSEs with positive SCE and direct them to reduce generation to return their SCE to zero as soon as possible. - Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
|  | Frequency above 60.10 and continuing to climb |
| 2 | If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE within five (5) minutes or no QSE appears to be hanging out: OR If no physical regulation down service is available: Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain 0 SCE) to reduce generation. Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to [QSE]. Reduce your generation by [MW amount] due to a High Frequency Excursion. Please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. Refer to 2.1.2 Verbal Dispatch Instructions (VDI) if necessary |
| 3 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4 | Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
| 5 | Log the actions that were taken. |

| ### 2.6.1 Issue an Operating Condition Notice (OCN) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Operating Condition Notice (OCN) IF: - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the National Hurricane Center. (http://www.nhc.noaa.gov/) - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - There is a projected capacity shortage or insufficient balancing bids. |
| 2 | Issue an OCN: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of OCN. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an OCN for [state OCN]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.2 Issue an Advisory |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Send to TDSPs and QSEs for information purposes. However ERCOT may increase ancillary service requirements or increase the Day Ahead market to two days ahead. Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Advisory IF: - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the National Hurricane Center. (http://www.nhc.noaa.gov/) - When ERCOT recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - When weather or ERCOT System conditions require more lead-time than the normal Day Ahead market allows. - Transmission system conditions indicate ERCOT is likely to exceed established limits that would ensure reliability in the occurrence of a single event (ERCOT is likely to exceed first Contingency Criteria). - A situation is emerging that has the reasonable expectation of leading ERCOT into an insecure state. - Loss of communications or control condition is anticipated or significantly limited. - If ERCOT is unable to comply with any of the market timing deadlines in the Day Ahead or Adjustment Period, or omits one or more procedures in the scheduling process. (Protocols 4.8) - Adjusted Responsive Reserve is equal to or below 3000 MW. - When long-range notice (approximately 48 hours) is needed to ensure the secure operation of the ERCOT system, alert the Market Participants to a potential threat to reliable operations with the following: - Lead time for dual fuel generating units to prepare for fuel supply problems in the event of anticipated severe cold weather - Any other operational concerns |
| 2 | Issue an Advisory: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of Advisory. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory for [state Advisory]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.3 Issue an Alert |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| NOTE: | ERCOT must issue an ALERT before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services, or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Alert IF: - Transmission system conditions are such that ERCOT is expected to exceed limits established to keep ERCOT within the limits of First Contingency Criteria; - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition; - Conditions have developed such that additional Ancillary Services are needed in the Operating Period; - There is a hurricane in the Gulf with expected landfall in Texas; - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - A situation is emerging that will have an adverse effect on grid reliability. - Loss of communications or control condition is pending or in progress. - Adjusted Responsive Reserve is equal to or below 2500 MW. - ERCOT holds two (2) consecutive Real-Time Balancing intervals. |
| 2 | Issue an Alert: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Alert. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Alert for [state Alert]. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.4 Issue an Emergency Notice |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notifications. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A transmission condition has been identified that requires emergency energy from any of the South DC-Ties. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no market alternatives exist to relieve the condition. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no timely solution is available from the market. - ERCOT has determined a fuel shortage exists. - ERCOT varies from requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures. |
| 2 | Issue an Emergency Notice: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Emergency Notice. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.5 Termination of Notification |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Advisory, Alert, or Emergency Notice will constitute cancellation of the previous notification. OCNs do not require a termination notification. |
| 1 | Update cancellation notice: - On the ENS - On the MIS - Notify QSEs via the Hotline |
| 2 | Using the Hotline, notify all QSEs when notice has been canceled. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is canceling the [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaRs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |

| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| --- | --- |
| 1b | Using the hotline, notify all QSEs to implement EECP STEP 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 1, QSEs are to enact the following”: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - Start and load all available RMR units to full capacity within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 1e | Ensure all available Non-Spin has been deployed. |
| 1f | Notify the ERCOT DC-Tie Desk of the EECP status. |
| 1g | VERIFY and log the following as appropriate: - All RMR units are at, or being loaded to, full capacity - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources - Available DC Tie capacity not being used by the market has been applied to the system. (Generally, this will not affect export schedules out of the ERCOT Control Area.) |

| 2a | In addition to measures associated with STEP 1 Implement EECP Step 2 IF: - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| --- | --- |
| 2b | Using the hotline, notify all QSEs to implement EECP STEP 2. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP STEP 2; ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs to deploy all Loads acting as a Resource (LaaRs) bid to supply Responsive Reserves Service within ten (10) minutes. Also: - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed,” [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TO via the Hotline that LaaRs have been deployed. |
| 2d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2e | Ensure the following: - EECP Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 is posted on the Market Information System (MIS) |
| 2f | Notify the DC-Tie Desk of change EECP status. |
| 2g | Unless a media appeal is already in effect, ask the Shift Supervisor about the issuance of an appeal through the public news media for voluntary energy conservation. (See Shift Supervisors procedures) |
| 2h | Dispatch any unutilized remaining capacity. |
| 2i | VERIFY and log the following as appropriate: - RMR units are at, or being loaded to full capacity. - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources. - LaaRs have been deployed. |

| NOTE: | EILS Resources have 10 minutes to comply with this instruction. If conditions develop that require implementing EECP step 4, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| --- | --- |
| 3a | In addition to measures associated with STEP 1 & 2; imPLEMENT eecp sTEP 3 IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. |
| 3b | Using the hotline, notify all QSEs to implement EECP STEP 3. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 3. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources in the current time period until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| 4a | In addition to measures associated with STEP 1 & 2,3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| --- | --- |
| 4b | Using the hotline, notify all QSEs to implement EECP STEP 4. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 4. Transmission Operators have been instructed to shed <MW Amount> of firm load. All QSEs confirm that their generation resources are at maximum output. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 4d | Notify the ERCOT DC-Tie Desk of change in EECP status. |
| 4e | In conjunction with the Transmission & Security Desk Operator, - Ensure EECP Step 4 is posted on the Emergency Notification System (ENS) short version – 32 characters - Ensure EECP Step 4 is posted on the Market Information System (MIS) |
| 4f | VERIFY the following: - All Generation Resources are at full capacity - All RMR units are at full capacity - Available Non-Spin has been deployed in the period of the emergency. - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended. - Available DC Tie capacity not being used by the market has been applied to the system - SPP Security Coordinator has been updated on ERCOT’s status - All LaaRs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

| ### 2.6.7 Restore EECP Steps |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | The Frequency Control Desk will implement applicable steps of the EECP Restoration. Numbering of procedure steps is reversed to coincide with EECP Steps. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaRs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| 4a | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. |
| 4b | Move from EECP STEP 4 to STEP 3 when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored. |
| 4c | Using the hotline, notify all QSEs of the reduction from EECP Step 4 to Step 3: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EECP Step 4 to Step 3.” QSEs that deployed Loads acting as a Resource (LaaRs) in EECP Step 2 may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4e | Ensure the following: - EECP Step 4 to Step 3 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 4 to Step 3 is posted on the Market Information System (MIS) |
| 4f | Notify the ERCOT DC-Tie Desk of change in EECP status. |
| 4g | Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LaaRs are being restored. |
| 4h | Instruct the Transmission & Security Desk Operator to notify the TOs that LaaRs are being restored. |

| 3a | Move from EECP STEP 3 to STEP 2 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |
| --- | --- |
| 3b | Using the hotline, notify all QSEs of the reduction from EECP Step 3 to Step 2: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EECP Step 3 to Step 2. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following: - EECP Step 3 to Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 3 to Step 2 is posted on the Market Information System (MIS) |
| 3e | Appeals through the public news media for voluntary energy conservation may be terminated. (See Shift Supervisor desk procedure) |

| 2a | Move from EECP Step 2 to Step 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW AND - All LaaRs have been restored or replaced with generation. |
| --- | --- |
| 2b | Using the hotline, notify all QSEs of the reduction from EECP Step 2 to Step 1: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EECP Step 2 to Step 1. QSE’s that deployed Emergency Interruptible Load Service (EILS) Resources in EECP Step 3 may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following steps are complete: - EECP Step 2 to Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 to Step 1 is posted on the Market Information System (MIS) |
| 2e | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS is being recalled. |
| 2f | Notify the ERCOT DC-tie Desk of change in EECP status. |

| 1a | Move from EECP Step 1 to Termination when: - EILS resources have been recalled. AND - All uncommitted units secured in EECP STEP 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |
| --- | --- |
| 1b | Using the hotline, notify all QSEs of the reduction from EECP Step 1 to termination: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is terminating EECP. An Alert still remains in effect. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following: - EECP Step 1 termination is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 termination is posted on the Market Information System (MIS) |
| 1e | Notify the ERCOT DC-Tie Desk of change in EECP status. |

| ### 2.6.8 Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify all QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Using the Hotline to issue the alert, notify all QSEs when Adjusted Responsive Reserve falls below 2500 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. Suspend all ERCOT required generation unit testing. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with an OOMC VDI for settlements. - Deploy Non-Spin and “Quick Start” GTs as follows: - Deploy Non-Spin if available. - If Non-Spin is unavailable or if all Non-Spin has been utilized, dispatch to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. Deplete these resources before proceeding to c. - If all “Quick Start” GTs that were “On” are depleted, OOMC/OOME the remainder of the “Available” “Quick Start” units. Deplete these resources before proceeding to d. If all “Quick Start” units are depleted, OOMC/OOME any additional “Available” units. |

| ### 2.6.9 Diminishing Reserve Notice Cancellation Guidelines |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
|  | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
|  | As system conditions permit, recall/release incrementally, any additional generation that was brought online to recover ARR. |
|  | Cancel an Alert or Advisory when: - All related OOM and Non-spin deployments have ended, AND - ARR is >= 3200 MW, AND - Load is trending down, OR - The MAI shows the “Max Cap Room” increasing over the next two hours |
|  | IF an alert has been canceled, - NOTIFY QSEs that testing may be resumed. Typical scripts: Cancel Advisory - “This is ERCOT operator [first and last name]. ERCOT is canceling the Advisory for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 3000 MW. [QSE] please repeat this directive back to me. That is correct, thank you.” Cancel Alert - “This is ERCOT operator [first and last name]. ERCOT is canceling the Alert for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 2500. MW. At this time, performance testing may resume. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
|  | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.10 Use of LaaRs to Arrest a Reportable Low Frequency Disturbance |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event: |
| NOTES: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than scheduled frequency prior the disturbance. Within 90 minutes ERCOT shall fully restore its Contingency Reserves to the pre-contingency level. This 90 minute restoration period begins at the end of the disturbance recovery period. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1083 MW , OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1083 MW. It is anticipated that the deployment of LaaRs will occur in stages. LaaRs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, a text message may be sent as time permits so as not to impede system operations. In order to control frequency, be prepared to issue a “Fleet Down” VDI once the system has recovered to its scheduled/pre-disturbance frequency value. |
| 1 | When a low frequency disturbance occurs due to a loss of generation, DETERMINE immediately, by calculating the loss of generation, if the event is potentially a NERC Reportable DCS Event. |
| 2 | If a low frequency disturbance occurs, AND there is no indication of a generation loss, assume that a potential DCS event has occurred and SCADA communications has been lost. - Determine the magnitude of the event by using the “ERCOT Interconnection Control Error” tag on the “ERCOT & QSE Summary Page” in PI. - Take care to calculate the entire generation loss from the PI tag, not just the difference between zero and the lowest number. Example: If the “ERCOT Interconnection Control Error” pre-disturbance value is +150 MW, and post disturbance value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. |
| 3 | If the “ERCOT Interconnection Control Error” post-disturbance value is greater than 1000 MW, implement Step 5. |
| 4 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 5 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - When system conditions warrant, issue a VDI using the hotline instructing QSEs to deploy ALL un-deployed LaaRs and hydro generation that are bid to supply Responsive Reserve. Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs and instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure printed Hotline Log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 7 | Complete the VDI form (Appendix 3) and process. - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows: “All QSEs are required to deploy any un-deployed LaaRs and hydro supplying Responsive Reserve due to a potential DCS event.” |
| 8 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being deployed. |
| NOTE: | verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| 9 | Restore LaaRs incrementally as system conditions permit. |
| 10 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being restored. |

| ### 2.6.11 Response to Frequency Decay |  |
| --- | --- |
|  | ###### Procedural Steps |
| PURPOSE: | Response to severe frequency decay, up to and including, using EECP Step 2 and the deployment of LaaR. |
| NOTE: | UFRs will deploy as follows: Hydro RRS - 59.90 Hz RRS LaaR – 59.7 Hz Sandow LaaR – 59.8 Hz |
| 1 | If Regulation Service is depleted, AND frequency is below 59.97 Hz and continues to decay, implement the following actions as necessary: - Ensure any remaining Balancing Energy is deployed. - OOME all RMR units that are online to full capacity. - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available. - When issuing the VDI, the operator should request enough generation to restore frequency and recall approximately 50% of Regulation Up Service. |
| 2 | VERIFY that the Balancing Offset is set to an approximate value that will restore Regulation Service. |
| 3 | IF frequency continues to decay, ENSURE 33% of the TOTAL Responsive Reserve Service is deployed (approximately 760 MW). |
| NOTE: | On depletion of the first 33% of TOTAL Responsive Reserve, ERCOT shall declare EECP in effect (Protocols Section 6.7.3). |
| 4 | IF Step 3 of this procedure does not arrest the frequency decay AND frequency reaches 59.85, IMPLEMENT EECP Step 2 and deploy ALL LaaR bid to supply Responsive Reserve. |
| 5 | Follow EECP Procedures as required per section 2.6.6. |
| NOTE: | Verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| NOTE: | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook – ERCOT – TrueTime Frequency |
| 6 | If Regulation Service is temporarily unavailable, AND frequency is below 59.91 Hz and continues to decay, implement the following action as necessary: - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available to recover frequency. - When issuing the VDI, the operator should request enough generation to restore frequency. |
| 7 | When Regulation Service is available, back in service and the frequency is normal, release the Fleet VDI. |

| ### 2.7.3 Approve NERC Tags for Railroad DC Tie and Laredo VFT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | Currently the Eagle Pass DC Tie (DC_S) is not available for commercial operation. Only emergency schedules can flow across the Eagle Pass tie. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-tags. |
| PURPOSE: | A NERC Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments. |
| 1 | When a new or updated tag is received in the OATI WebTrans system: - Determine if the following information is correct on the NERC E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the NERC E-Tag, deny the tag, otherwise go to Step 1.2. - Determine if one or more NERC E-Tags being submitted will cause the DC Tie to exceed the schedule MW limit for the tie. - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the schedule MW limit for the tie. - Curtail the NERC E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the schedule MW limit for the tie. - Determine if the tag passed or failed validation. - If the tag passes validation, go to Step 2. - If the tag fails validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag fails validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve a NERC E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the tag approval timeline, the tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the tag to the schedule: - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E-Tag. - If the tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” bow will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

| ### 2.7.6 Curtailment for Road DC Tie and Laredo VFT |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE: | Scheduling limits for the ROAD DC Tie and Laredo VFT can change due to changes in generation, transmission configuration, weather, and other system conditions. After receiving the import/export limits for next day, it may be necessary to curtail schedules. |
| 1 | If a scheduling limit changes that causes the DC Tie(s) to be overscheduled, review the NERC E-Tags and curtail to the amount needed based on Last-in-First-Out (LIFO) until under the scheduling limit of the DC tie. |
| 2 | Coordinate with the DC Tie Operator to ensure that CFE approves the curtailment. |
| 3 | If a QSE requests a tag to be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |

| ### 2.7.7 Managing and Documenting Daily Inadvertent for North and East DC-Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties |
| NOTE: | Due to a deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW out of ERCOT and into SPP, OR - Add MW flow in the direction of the schedule |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5. | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

| ### 2.7.8 Managing and Documenting Daily Inadvertent for the Eagle Pass, Laredo and Railroad DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ROAD_DC, or LAR_VFT) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). The Eagle Pass DC Tie is not available for commercial operation at this time. The normal scheduled and actual values should be zero (0) However if emergency energy flowed actual values will exist. |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Corpus Christi TSP for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - Give the integrated actual value for the Eagle Pass, Laredo and Railroad DC Ties indicated on the “Tie Data” display in WebTrans. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. No further action is required. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values: - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, instruct the DC Tie Operator to change their value to match ERCOT’s value. WebTrans Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the South DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

| ### 2.7.11 EEA 1 Schedule across the SPP DC Ties for EEA 1 (EECP 1) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | Notify the SPP Reliability Coordinator of ERCOT’s EEA 1 status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. We will contact the Tariff desk to inquire about the availability of transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2, proceed to Section 2.7.7 If there is transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the transmission service available. Thank you.” |
| NOTE: | SPP will contact PSEs with unscheduled reservations and notify them of ERCOT’s EEA 1 status. PSEs may choose to use their reservation to schedule into ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers): Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. - If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-tag(s) and proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify the DC Tie Operator of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag (s) for an EEA 1 schedule. |

| ### 2.7.12 Emergency Energy Request across the SPP DC Ties for EEA 2 or 3 (EECP 2 - 4) |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE: | If ERCOT goes directly to an EEA 2 or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below. |
| 1 | Notify the SPP Reliability Coordinator: Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will contact the Tariff desk to inquire about the availability of emergency transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the emergency transmission service available. Thank you.” |
| NOTE: | ERCOT must have the RCIS updated with the EEA 2/3 status before granting emergency transmission service. |
| NOTE: | SPP will curtail all non-firm transmission service schedules going out of ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-tag(s). Proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status: Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| NOTE: | Keep SPP informed of ERCOT’s status. |

| ### 2.7.13 Backing out of EEAs and Termination |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| 1 | When moving EEA status: Notify the SPP Reliability Coordinator of ERCOT’s status. Typical script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify the Tariff desk, please transfer me. Thank you.” |
| 2 | Notify the SPP Tariff desk of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify AEP. Thank you.” |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| NOTE: | Repeat above steps with the notifications until ERCOT’s status is EEA 0 (zero). |