## Power Operations Bulletin # 402

ERCOT has revised the Frequency Control Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

| ### Issue an Alert |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| NOTE: | ERCOT must issue an ALERT before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services, or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Alert IF: - Transmission system conditions are such that ERCOT is expected to exceed limits established to keep ERCOT within the limits of First Contingency Criteria; - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition; - Conditions have developed such that additional Ancillary Services are needed in the Operating Period; - There is a hurricane in the Gulf with expected landfall in Texas; - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - A situation is emerging that will have an adverse effect on grid reliability. - Loss of communications or control condition is pending or in progress. - ERCOT holds two (2) consecutive Real-Time Balancing intervals. |
| 2 | Issue an Alert: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Alert. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Alert for [state Alert]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.4 Issue an Emergency Notice |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notifications. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no market alternatives exist to relieve the condition. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no timely solution is available from the market. - ERCOT has determined a fuel shortage exists. - ERCOT varies from requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures. |
| 2 | Issue an Emergency Notice: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Emergency Notice. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

| ### 2.6.6 Implement EECP |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Frequency Control Desk will implement applicable steps of the EECP. EECP STEPS in this procedure are to be implemented in concert with the Transmission & Security Desk EECP procedures. Public media appeals may be enacted prior to EECP as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaRs as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any step of EECP is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EECP Step 4. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EECP Step 4. |

| 1a | Implement EECP Step 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| --- | --- |
| 1b | Using the hotline, notify all QSEs to implement EECP STEP 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 1, QSEs are to do the following: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. - ERCOT ISO is reminding you, if you have not already done so, to schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following: - EECP Step 1 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 1 is posted on the Market Information System (MIS) |
| 1e | Ensure all available Non-Spin has been deployed. |
| 1f | Notify the ERCOT DC-Tie Desk of the EECP status. |
| 1g | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources - Available DC Tie capacity not being used by the market has been applied to the system. (Generally, this will not affect export schedules out of the ERCOT Control Area.) |

| 2a | In addition to measures associated with STEP 1 Implement EECP Step 2 IF: - EECP Step 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| --- | --- |
| 2b | Using the hotline, notify all QSEs to implement EECP STEP 2. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP STEP 2; ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs to deploy all Loads acting as a Resource (LaaRs) bid to supply Responsive Reserves Service within ten (10) minutes. Also: - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed,” [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TO via the Hotline that LaaRs have been deployed. |
| 2d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2e | Ensure the following: - EECP Step 2 is posted on the Emergency Notification System (ENS) short version – 32 characters - EECP Step 2 is posted on the Market Information System (MIS) |
| 2f | Notify the DC-Tie Desk of change EECP status. |
| 2g | Dispatch any unutilized remaining capacity. |
| 2h | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed in the expected period of the emergency. - Available uncommitted units have been dispatched and loaded as necessary. - Testing has been suspended on all resources. - LaaRs have been deployed. |

| NOTE: | EILS Resources have 10 minutes to comply with this instruction. If conditions develop that require implementing EECP step 4, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to all QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| --- | --- |
| NOTE: | Unless a media appeal is already in effect, one is required in this step. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation. |
| 3a | In addition to measures associated with STEP 1 & 2; imPLEMENT eecp sTEP 3 IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. If no EILS exist, skip EECP step 3 and proceed to EECP step 4 if needed. |
| 3b | Using the hotline, notify all QSEs to implement EECP STEP 3. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 3. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources in the current time period until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4a | In addition to measures associated with STEP 1 & 2,3; Implement EECP Step 4 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| 4b | Using the hotline, notify all QSEs to implement EECP STEP 4. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EECP Step 4. Transmission Operators have been instructed to shed <MW Amount> of firm load. All QSEs confirm that their generation resources are at maximum output. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 4d | Notify the ERCOT DC-Tie Desk of change in EECP status. |
| 4e | In conjunction with the Transmission & Security Desk Operator, - Ensure EECP Step 4 is posted on the Emergency Notification System (ENS) short version – 32 characters - Ensure EECP Step 4 is posted on the Market Information System (MIS) |
| 4f | VERIFY the following: - All Generation Resources are at full capacity - Available Non-Spin has been deployed in the period of the emergency. - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended. - Available DC Tie capacity not being used by the market has been applied to the system - SPP Security Coordinator has been updated on ERCOT’s status - All LaaRs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

| ### 2.6.8 Provide Advanced Notice of Diminishing Responsive Reserve |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves. |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify all QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Using the Hotline to issue the alert, notify all QSEs when Adjusted Responsive Reserve falls below 2500 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. - Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. - Suspend all ERCOT required generation unit testing. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Deploy Non-Spin if not already utilized. |
| 5 | OOME to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with an OOMC VDI for settlements. |

| ### 2.6.12 Loss of Primary Control Center Functionality |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | This procedure is to be performed by the Operator at the Back-up Control Center (BCC) in the event that: - Functionality of the Primary Control Center (PCC) is lost OR - Communication with the PCC is lost OR - As directed by the Shift Supervisor. |
| Contact Security | IF: - You are unable to reach any Operators at the PCC, THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the BCC - Notify them of the situation AND - Have them attempt to make contact with Security at TCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This is ERCOT operator [first and last name], ERCOT is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This is ERCOT operator [first and last name], ERCOT is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support, Telecommunications - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Most potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website: http://www.ercot.com/content/gridinfo/transmission/docs/ERCOT_Contingency_GRPList_2003.xls |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and Thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |

| ### 2.6.13 Restoration of Primary Control Center Functionality |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | This procedure is to be performed by the Frequency Control Desk Operators at the Back-up Control Center (BCC) in restoring Real-Time operations. - Additional staff has arrived, including a Shift Supervisor, - BCC has become PCC, - All EMS applications up and functioning properly |
| NOTE: | As additional Operators arrive, be sure to communicate any pertinent information that will assist them in getting their specific functions ready for normal operation. |
| Restoring Frequency Control | When an Operating Period Desk Operator has arrived, had time to get the offset calculation spreadsheet caught up, and is able to enter offset values into the MOI: IF: - Holding Real-time Balancing Energy Market (RTB) deployments, THEN: - Verify the proper operation of the RTB and that deployments are being sent to the Market Participants (MP) AND - Remove the QSE that is put on constant frequency. |
| Market Notification | IF: - RTBM is running and valid deployments are being sent, THEN: - Place the following QSE Hotline call: * * * WARNING * * * When removing a QSE from constant frequency control, remove ERCOT AGC from Monitor mode. Typical Script: “This is ERCOT operator [first and last name], ERCOT is resuming normal, Real-Time operations from the back-up control center. Please continue to direct all phone calls to (512) 225-7100. ERCOT is ending VDI [#] at [time]. Resume with the [interval ending time] Balancing Energy deployments. [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Additional Notifications | Notify the following: - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations and/or designee - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Notification of Additional Operators | When: - All functionality has been resumed at the BCC, THEN: - Notify the additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System. |
| Contact Security | - Notify Security that the transition of Operations to the BCC has been completed |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |

| ### Approve NERC Tags for SPP DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| PURPOSE: | A NERC Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments. |
| NOTE: | AEP TO in Columbus, Ohio is the Tie Operator for the East and North DC Ties. The designation in WebTrans for the East tie is DC_E and the North tie is DC_N. |
| NOTE: | Each time a new or updated NERC E-Tag is submitted, the WebTrans system will automatically validate the NERC E-Tag. WebTrans will display whether the NERC E-Tag has passed or failed validation. The criteria ERCOT uses to validate NERC E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the NERC E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated NERC E-Tag. Currently the only validation criterion set to automatically deny a NERC E-Tag is “QSE Contract”. If this validation fails the NERC E-Tag will be automatically denied. If you feel a tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/docs/QSEs.xls Select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the tag and inform the OATI help desk. WebTrans Reference Display: Tag Criteria Summary |
| 1 | When a new or updated tag is received in the OATI WebTrans system: 1.1 Determine if the following information is correct on the NERC E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - “ERCOT-E” or “ERCOT-N” is selected for the correct Point-of-Receipt (POR) or Point of Delivery (POD) portion of the physical path. - “CSWS” is included as a Scheduling Entity on the SWPP TP row in the physical path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the physical path. - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new tag must be on a quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the NERC E-Tag, deny the tag, otherwise go to Step 1.2. 1.2 If one or more NERC E-Tags are submitted that will cause the DC Tie to be overscheduled: - Contact SPP to ensure they also see the over-schedule and they will ensure the appropriate actions are taken to correct the over-schedule. Also inform SPP that if the appropriate actions to correct the over-schedule are not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the NERC E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. - IF a NERC E-Tag is curtailed to zero (0) due to an over-schedule that was not corrected in time, contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. 1.3 Determine if the tag passed or failed validation. - If the tag passes validation, go to Step 2. - If the tag fails validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag fails validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve a NERC tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the tag approval timeline, the tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the tag data to the schedule: - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the NERC E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E-Tag. - If the tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |

| ### 2.7.2 Import and Export Limits for the CFE DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored Sheet”. |
| 1 | After midnight, verify that the daily import and export limits have been updated in RTMONI and are displayed correctly on the ERCOT website at: http://mospublic.ercot.com/ercot/jsp/frequency_control.jsp |
| 2 | Verify the limits with the DC-Tie Operator. |

| ### 2.7.3 Approve NERC Tags for the CFE DC Tie |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-tags. |
| PURPOSE: | A NERC Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments. |
| 1 | When a new or updated tag is received in the OATI WebTrans system: - Determine if the following information is correct on the NERC E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new tag must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the NERC E-Tag, deny the tag, otherwise go to Step 1.2. - Determine if one or more NERC E-Tags being submitted will cause the DC Tie to exceed the schedule MW limit for the tie. - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the schedule MW limit for the tie. - Curtail the NERC E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the schedule MW limit for the tie. - Determine if the tag passed or failed validation. - If the tag passes validation, go to Step 2. - If the tag fails validation and the NERC E-Tag was automatically denied (QSE Contract), no further action is required. - If the tag fails validation and the NERC E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve a NERC E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the tag approval timeline, the tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the tag to the schedule: - If the tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the NERC E-Tag. - If the tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the NERC E-Tag. - If the tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the NERC E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

| ### 2.7.5 Curtailment of SPP DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | When a curtailment alarm is received in WebTrans, - Approve the tag curtailment. WebTrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| 2 | If a QSE or SPP requests a tag be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |
| NOTE | Tag curtailments must be in an “Approved” or “Implemented” status to be calculated Into the Net Scheduled Interchange (NSI) |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by NERC E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

| ### 2.7.6 Curtailment for the CFE DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE: | Scheduling limits for the CFE DC Ties can change due to changes in generation, transmission configuration, weather, and other system conditions. After receiving the import/export limits for next day, it may be necessary to curtail schedules. |
| NOTE: | If any of the DC-Ties trip, ERCOT will have the responsibility to curtail the schedules. |
| 1 | If a scheduling limit changes that causes the DC Tie(s) to be overscheduled, review the NERC E-Tags and curtail to the amount needed based on Last-in-First-Out (LIFO) until under the scheduling limit of the DC tie. |
| 2 | Coordinate with the DC Tie Operator to ensure that CFE approves the curtailment. |
| 3 | If a QSE requests a tag to be curtailed or adjusted for any reason, curtail the tag to 0 (zero). |

| ### 2.7.7 Managing and Documenting Daily Inadvertent for the SPP DC-Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties |
| NOTE: | Due to a deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW out of ERCOT and into SPP, OR - Add MW flow in the direction of the schedule |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5. | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

| ### 2.7.8 Managing and Documenting Daily Inadvertent for the CFE DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a NERC E-Tag is created and submitted, the tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ROAD_DC, or LAR_VFT) or if ERCOT is left off the NERC E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the NERC E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the NERC E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The NERC E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Corpus Christi TSP for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each NERC-E-Tag ID and MW amount for the affected DC Tie(s). - If a NERC E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the NERC E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - Give the integrated actual value for the Eagle Pass, Laredo and Railroad DC Ties indicated on the “Tie Data” display in WebTrans. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. No further action is required. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values: - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, instruct the DC Tie Operator to change their value to match ERCOT’s value. WebTrans Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the CFE DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

| ### 2.7.10 Emergency Energy across the CFE DC Ties |  |
| --- | --- |
| ###### Step # | ###### Procedural Steps |
| NOTE: | ERCOT must declare an alert or emergency and make the proper posting/hotline call when receiving emergency energy. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| NOTE: | Transmission Emergencies will be coordinated with the ERCOT Transmission & Security Desk. |
| NOTE: | The Railroad and Eagle Pass DC-Ties and Laredo VFT are not for commercial use at this time, skip steps 2 and 3. Step 4 will apply to all CFE DC-Ties. |
| 1 | ERCOT and/or CFE will contact the DC-Tie Operator (AEP TO in Corpus) to verify if power is available for transfer on any of the CFE DC-Ties. If energy is available for transfer, determine the DC-Tie(s), MW amount, time and duration (if possible). |
| 2 | For emergency energy to flow across the CFE DC-Ties, notify AEP (SQ4) QSE with the information listed in step 1 to enter the E-Tag. |
| 3 | Issue AEP QSE (Generation Dispatchers) a VDI for the emergency energy. Forward to Shift Supervisor (fax) as time permits. |
| 4 | Emergency energy across the CFE DC-Ties do not need an E-Tag submitted. Issue AEP QSE (Generation Dispatchers) a VDI and coordinate with the DC-Tie Operator. |