Power Operations Bulletin # 405

ERCOT has revised the Frequency Control Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

1.	Introduction

## 1.1	Purpose

This Procedure provides the System Operator assigned to the Frequency Control Desk with detailed procedures required for performing duties assigned to that position.  The ERCOT Frequency Control Desk is responsible for ensuring that sufficient generation is available and on-line to cover load and meet reserve requirements, such that the frequency within the ERCOT System remains within the tolerances specified by the Protocols and NERC, for the current Operating Day.

The ERCOT Frequency Control Desk monitors load and generation for the current operating hour.

## 1.2	Scope

The instructions contained in this procedure are limited to those required for the ERCOT Frequency Control Desk.  Instructions for other ERCOT control room positions are contained in separate procedures, one for each position.  This procedure does not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and to perform any other duties as required or requested by appropriate ERCOT supervision.

## 1.3	Roles/Responsibilities

ERCOT Shift Supervisor

The ERCOT Shift Supervisor is responsible for supervision of the ERCOT Frequency Control Desk position and may at times be responsible for performing the procedures contained in this manual.

ERCOT System Operator, Frequency Control Desk

The ERCOT System Operator – Frequency Control Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

  - Reliability Coordinator.

  - Balancing Authority

  - Transmission Operator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT electric system.  These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

## 1.4	General Duties

- a. Respond to Market Participant Questions and Issues.

b. Receive questions and issues from Market Participants as they are     submitted.

c. Respond to Market Participant questions and issues when appropriate information is available.

2. Post required notices to the Market as stated in this procedure.  If unable to timely post a notice, then any other Operator or Shift Supervisor may post it.

# 2.1 	Monitor Generation

# 2.1.1 Control Generation to Ensure Load Is Covered

Procedure Purpose: To determine if there is enough generation to cover the load forecast.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Monitor the current ERCOT System Load and Short Term Load Forecast. Reference Displays: Generation Area Status Short-Term Load Forecast Excel MAI (Market Analysis Interface) |
| 2 | Determine that the current ERCOT System generation capacity is sufficient to meet the Short-Term Load Forecast requirements. Reference Displays: Generation Area Status Excel MAI (Market Analysis Interface) |
| 2a | Compare the current generation and load with the planned capacity values from resource plan at least every other hour. Reference Displays: Generation Area Status Daily Operation Plan – Resource Plan Excel MAI (Market Analysis Interface) |
| 2b | If real-time generation is approaching planned capacity a possible shortage is developing. Discuss situation with Operating Period Desk and Shift Supervisor, and increase monitoring of reserves. Reference Displays: Generation Reserve Status – Available Details Real Time Balancing Market – Balance Bid Tab Real Time Balancing Market – QSE Tab Excel MAI (Market Analysis Interface) |
| 3 | If a shortage is developing in the next hour, consider OOMC or deploying of Non-Spinning Reserve Service. Consult with the Operating Period Desk regarding hour-ahead study results. |
| 4 | If OOMC is decided upon, request the Transmission & Security Desk perform the actual instruction. If NSRS is decided upon, request the Operating Period Desk perform the actual instruction. |
| 5 | MONITOR additional available generation capacity and available DC tie capacity. Evaluate amount of additional capacity available in a short time frame using telephone communications to QSEs as appropriate. Reference Displays: Generation Area Status Generation Reserve Status Generation Tie-Line Status |
| 6 | Monitor Responsive Reserves on the QSE Reserve Status Display. If Adjusted Responsive Reserve plus LaaRs is correctly calculated, and is below 2300 MW, - notify the Shift Supervisor - implement EEA - log in the Operator’s Log any decision to declare an EEA |
| 7 | Monitor Ancillary Service Obligations If a QSE is not meeting its Ancillary Services obligations as shown on the QSE Reserve Status Display, - contact the QSE to correct the deficiency - notify the Shift Supervisor of the QSE’s response log the activities performed in connection with this step |

# 2.1.2	Three Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |

# 2.1.3	Verbal Dispatch Instructions (VDI)

Procedure Purpose: Issue A VDI to QSE(s) to give a directive

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | VDIs should not re-iterate an instruction given via XML. |
| NOTE: | Whenever a VDI is issued, request the QSE to repeat back the instructions. IF the QSE Hotline is used to issue a VDI, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the instructions and direct a repeat back again. Continue until an acceptable repeat back is received. |
| 1 | As time permits, complete the VDI form (See Desk Top Guide Section 7.4). The following are required fields on all VDIs: - VDI # - EXAMPLE: For the 4th VDI issued by the Frequency Control Desk on May 01, 2009 the number would appear as “F-050109-04” - Operating Day - ERCOT System Operator - Receiving Entity - Receiving Entity’s Operator - Time & Date - Instruction - Reason for Instructions - Intervals - Repeated Instruction back - ERCOT Operator’s signature Blank fields are to have N/A entered. |
| 2 | LOG in the Operator’s Log the VDI information and information relevant to the decision for issuing the VDI. |
| 3 | Forward the VDI form to the Shift Supervisor, as time permits. |

# 2.1.7	Replacing Responsive Reserve through a Bilateral Trade

Procedure Purpose: Process to monitor a QSEs obligation to maintain their Responsive Reserve commitments through a bilateral trade with another QSE.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | A QSE has the option to reduce their base power schedule and replace the difference from the balancing market. This will allow the QSE to back down their generation so they can provide their Ancillary Service obligation. (REF. PRR 404) |
| NOTE: | When a resource (either LaaR or generation) that is supplying RRS becomes unavailable to a QSE (QSE A) and needs to be replaced through a Bilateral Trade with another QSE (QSE B), then QSE A is expected to inform ERCOT. |
| 1 | Obtain the following information from QSE A: - Intervals affected - Name of QSE with whom the bilateral trade was made |
| 2 | IF the resource that became unavailable was a LaaR, then ENSURE QSE B maintains an amount of Responsive Reserve Service equal to their own obligations PLUS the amount of the bilateral agreement with QSE A for the affected intervals. |
| 3 | If the QSEs response is not satisfactory, notify the Shift Supervisor so a determination of protocol violation can be made. LOG in the Operator’s Log the conversation, including the information provided. |
| 4 | Email the information to RRSList@ercot.com |

# 2.2.3 	Monthly Testing of Satellite Phone System

Procedure Purpose: Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Attachment B of the ERCOT Satellite Phone User Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form (See Desk Top Guide Section 7.7.3). An electronic copy of this form is located in P:\ SYSTEM OPERATIONS “Satellite Bridge Testing forms” folder. |
| 4 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is complete. |
| 5 | Log the test date and results in the ERCOT Operations Log. |
| NOTE: | Verify with the Shift Supervisor that the following personnel are notified for any Satellite phone problems during the test by e-mail: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |

# 2.4 Monitor SCE

# 2.4.1 	Monitor SCE for each QSE

Procedure Purpose: To ensure that QSE’s Schedule Control Error is maintained within acceptable limits and the telemetry is working correctly.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Compare QSE’s SCE with the ERCOT calculated SCE. If these two values differ significantly, and the cause is not already known, review SCE components with the QSE to determine the source of the disagreement. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 2 | When the source of disagreement is established, decide which end (QSE or ERCOT) is most likely in error. If the error is on the ERCOT end, call technical support if appropriate. If the error is on the QSE end, request that the QSE take corrective action. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 3 | If SCE for a QSE departs significantly from 0 for an unknown reason, or if a SCE violation is causing a security problem, call the QSE involved and determine the reason for the deviation. |
| 4 | If a wind only QSE SCE deviates significantly from 0 call the QSE and requested that they update their resource plan and base power schedules. The resource plans and base power schedules should be updated together and stay matched. Since base power changes are not allowed during the operating hour the SCE can not be corrected immediately. |
| 5 | If the QSE is unable to correct the problem, notify the Shift Supervisor. |
| 6 | LOG in the Operator’s Log the event, including the QSE name, the name of the person communicated with, the date and time of the conversation, magnitude, length, reason for the deviation and any other pertinent information. |

# 2.5	Frequency Control

# 2.5.1	Frequency Control Operating Procedure

Procedure Purpose: To maintain system frequency within acceptable levels.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| 1 | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or - “Last AGC Cycle” time on Generation Area Status display is not updating or AGC operation adversely impacts the reliability of the Interconnection If the problem can’t be resolved quickly, place a large QSE (that has regulation reserve) on constant frequency. |
| NOTE: | - In the scenario where AGC operation adversely impacts the reliability of the interconnection, (ERCOT is handing over the frequency control to a large QSE), ERCOT AGC should be placed into the MONITOR mode. |
| 2 | Using the Hotline, notify all QSEs that ERCOT is having computer issues and is putting a QSE on constant frequency. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is currently having computer issues and has put a QSE on constant frequency until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 3 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| NOTE: | If the QSE that is put on constant frequency is having trouble keeping up, issue fleet VDI’s to other QSE’s to help out or put a different QSE on constant frequency. Remember to take the first QSE off constant frequency. For low frequency refer to 2.5.2, Operator Instructions for Low Frequency. For high frequency refer to 2.5.5, Operator Instructions for High Frequency. |
| 5 | When frequency control is functioning, remove the QSE from constant frequency. |
| 6 | Notify all QSE’s by Hotline that ERCOT is back on control. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is back to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 7 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 8 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 9 | At the operator’s discretion, turn off SCE feedback for Regulation Providers with Participation Factors less than 1% (<0.01). |
| 10 | Monitor QSE generation and SCE: - Remove a QSE’s SCE feedback if they have a large SCE and their generation is not moving in the proper direction or rate to correct their SCE. Reference Display Responsive, Regulation, and SCE Regulation |
| 11 | NEVER (unless directed by the Control Engineer or designee): Modify “Total (SCE-responsive) Feedback Gain” (should be altered by the Control Engineer) - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) Reference Displays: Responsive, Regulation, and SCE – Details |
| 12 | LOG in the Operator’s Log frequency deviations of greater than or equal to 0.10 Hz. Record the following: - Possible reasons if known. (SCE, Large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped. - Approximate MW that was on the unit when the unit tripped. - Approximate ERCOT load. |

## 2.6.3	 Issue a Watch

Procedure Purpose: To inform the QSEs of a system Watch

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System |
| NOTE: | ERCOT must issue a Watch before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services, or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits established to keep ERCOT within the limits of First Contingency Criteria; - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition; - Conditions have developed such that additional Ancillary Services are needed in the Operating Period; - There is a hurricane in the Gulf with expected landfall in Texas; - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - A situation is emerging that will have an adverse effect on grid reliability. - Loss of communications or control condition is pending or in progress. - ERCOT holds two (2) consecutive Real-Time Balancing intervals. |
| 2 | Issue a Watch: - Post on the ENS - Post on the MIS - Notify QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Watch. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.5	 Termination of notification

Procedure Purpose: To inform the QSEs of a cancellation of a previous notification.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | \ |  |  |  |
|  | \ |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Advisory, Watch, or Emergency Notice will constitute cancellation of the previous notification. The termination of OCNs does not require a hotline call; however updating the ENS and MIS is necessary. |
| 1 | Update cancellation notice: - On the ENS - On the MIS - Notify QSEs via the Hotline |
| 2 | Using the Hotline, notify all QSEs when notice has been canceled. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is canceling the [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits |

## 2.6.6	Implement EEA

Procedure Purpose: To implement an Energy Emergency Alert(s) for the appropriate system conditions.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Frequency Control Desk will implement applicable levels of the EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaR as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any level of EEA is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3 |
| 1a | Implement EEA 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 1b | Using the hotline, notify QSEs to implement EEA 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 1, QSEs are to do the following: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 1 |
| 1e | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources |
| 2a | In addition to measures associated with EEA 1 Implement EEA 2A IF: - EEA 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 2b | Using the hotline, notify QSEs to implement EEA 2A. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2A; ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to QSEs to deploy all LaaRs bid to supply Responsive Reserves Service within ten (10) minutes. Also: - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that LaaR have been deployed. |
| 2d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2A |
| 2f | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources. - LaaRs have been deployed. |
| NOTE: | EILS Resources have 10 minutes to comply with this instruction. If conditions develop that require implementing EEA 3, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| NOTE: | Unless a media appeal is already in effect, one is required in this level. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation |
| 3a | In addition to measures associated with EEA 1 & 2A; imPLEMENT eEA 2B IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. If no EILS exist, skip EEA 2B and proceed to EEA 3 if needed. |
| 3b | Using the hotline, notify QSEs to implement EEA 2B. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2B. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources in the current time period until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that EILS Resources have been deployed. |
| 3d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2B |
| 4a | In addition to measures associated with EEA 1, 2A, & 2B; Implement EEA 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| 4b | Using the hotline, notify QSEs to implement EEA 3. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 3. Transmission Operators have been instructed to shed <MW Amount> of firm load. QSEs confirm that their generation resources are at maximum output. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 4d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 3 |
| 4e | VERIFY the following: - All Generation Resources are at full capacity - Available Non-Spin has been deployed - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended - All LaaRs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

## 2.6.7	Restore EEA

Procedure Purpose: Backing out and terminating Energy Emergency Alert(s).

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA Restoration. Numbering of procedure steps is reversed to coincide with EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. |
| 4a | Restore firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MW |
| 4b | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. Using the hotline, notify QSEs of the restoration of firm load: - When QSEs have answered the Hotline, print the Hotline log Typical script: “This is ERCOT operator [first and last name]. ERCOT is currently restoring firm load. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Move from EEA 3 to EEA 2B when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored. |
| 4d | Using the hotline, notify QSEs of the reduction from EEA 3 to 2B, if 2B was skipped move from EEA 3 to 2A : - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B.” QSEs that deployed LaaR in EEA 2A may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4e | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4f | Ensure the following is posted on the ENS and MIS: - EEA 3 to EEA 2B |
| 4g | Instruct the Transmission & Security Desk Operator to notify the TOs that LaaRs are being restored. |
| NOTE: | Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LaaRs are being restored |
| 3a | Move from EEA 2B to EEA 2A when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 3b | Using the hotline, notify all QSEs of the reduction from EEA 2B to EEA 2A: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - EEA 2B to EEA 2A |
| 3e | Instruct the Transmission & Security Desk Operator to notify the TOs that ERCOT moved from EEA 2B to EEA 2A. |
| 3f | Appeals through the public news media for voluntary energy conservation may be terminated, notify Shift Supervisor |
| 2a | Move from EEA 2A to EEA 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW AND - All LaaR have been requested to be restored or replaced with generation |
| 2b | Using the hotline, notify QSEs of the reduction from EEA 2A to EEA 1: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1. QSE’s that deployed EILS Resources in EEA 2B may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - EEA 2A to EEA 1 |
| 2e | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS Resources are being recalled. |
| 1a | Move from EEA 1 to EEA 0 when: - EILS Resources have been requested to be recalled AND - All uncommitted units secured in EEA 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 1b | Using the hotline, notify QSEs of the reduction from EEA 1 to EEA 0: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is terminating EEA. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - EEA termination |
| 1e | Instruct the Transmission & Security Desk Operator to notify the TOs of the termination of EEA. |

## 2.6.8	 Provide Advanced Notice of Diminishing Responsive Reserve

Procedure Purpose: Guidelines for issuing advance notice of diminishing Responsive Reserves

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory has been issued. |
| 4 | Ensure the following is posted on the ENS and MIS: - Advisory issued for ARR below 3000 MW. |
| 5 | When adjusted Responsive Reserve falls below 2500 MW: Using the Hotline, notify QSEs: - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing a Watch to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. - Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. - Suspend all ERCOT required generation unit testing. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure Non-Spin has been deployed. |
| 7 | OOME to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0. Follow up with a Settlements only VDI stating :OOMC for Quick-start” on the VDI form. |
| 8 | Instruct the Transmission & Security Desk Operator to notify the TOs that a Watch has been issued. |
| 9 | Ensure the following is posted on the ENS and MIS: - Watch issued for ARR below 2500 MW. |

## 2.6.9	 Diminishing Reserve Notice Cancellation Guidelines

Procedure Purpose: To provide notifications and back out of the actions taken during diminishing system reserves.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
| 1 | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
| 2 | As system conditions permit, recall/release incrementally, any additional generation that was brought online to recover ARR. |
| 3 | Cancel a Watch or Advisory when: - All related OOM and Non-spin deployments have ended, AND - ARR is >= 3200 MW, AND - Load is trending down, OR - The Excel MAI shows the “Max Cap Room” increasing over the next two hours |
| 4 | . IF a watch has been canceled, - NOTIFY QSEs that testing may be resumed. Typical scripts: Cancel Advisory - “This is ERCOT operator [first and last name]. ERCOT is canceling the Advisory for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 3000 MW. [QSE] please repeat this back to me. That is correct, thank you.” Cancel Watch - “This is ERCOT operator [first and last name]. ERCOT is canceling the Watch for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 2500. MW. At this time, performance testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 6 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory or Watch has been cancelled. |

## 2.6.10	 Potential DCS Event – Use of LaaRs to Arrest a Low Frequency Disturbance

Procedure Purpose: To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | There are times when the MW amount lost will be more than the NERC reportable amount. In these cases LaaRs will still need to be used to recover frequency |
| NOTE: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than scheduled frequency prior the disturbance. Within 90 minutes ERCOT shall fully restore its Contingency Reserves to the pre-contingency level. This 90 minute restoration period begins at the end of the disturbance recovery period. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1083 MW OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1083 MW. It is anticipated that the deployment of LaaRs will occur in stages. LaaRs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, a text message may be sent as time permits so as not to impede system operations. In order to control frequency, be prepared to issue a “Fleet Down” VDI once the system has recovered to its scheduled/pre-disturbance frequency value. |
| 1 | When a low frequency disturbance occurs due to a loss of generation, DETERMINE immediately, by calculating the loss of generation, if the event is potentially a NERC Reportable DCS Event. |
| 2 | If a low frequency disturbance occurs, AND there is no indication of a generation loss, assume that a potential DCS event has occurred and SCADA communications has been lost. - Determine the magnitude of the event by using the “ERCOT Interconnection Control Error” tag on the “ERCOT & QSE Summary Page” in PI. - Take care to calculate the entire generation loss from the PI tag, not just the difference between zero and the lowest number. Example: If the “ERCOT Interconnection Control Error” pre-disturbance value is +150 MW, and post disturbance value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. |
| 3 | If the “ERCOT Interconnection Control Error” post-disturbance value is greater than 1000 MW, implement Step 5. |
| 4 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 5 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - When system conditions warrant, issue a VDI using the hotline instructing QSEs to deploy ALL un-deployed LaaRs and hydro generation that are bid to supply Responsive Reserve. Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs and instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing a Verbal Dispatch Instruction instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure printed Hotline Log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 7 | Complete the VDI form (See Desk Top Guide Section 7.4) and process. - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows: “All QSEs are required to deploy any un-deployed LaaRs and hydro supplying Responsive Reserve due to a potential DCS event.” |
| 8 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being deployed. |
| NOTE: | verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| 9 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being restored. |

## 2.6.11	 Response to Frequency Decay

Procedure Purpose: Response to severe frequency decay, up to and including, using EEA 2A and the deployment of LaaR.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | UFRs will deploy as follows: Hydro RRS - 59.90 Hz RRS LaaR – 59.7 Hz Sandow LaaR – 59.8 Hz |
| 1 | If Regulation Service is depleted, AND frequency is below 59.97 Hz and continues to decay, implement the following actions as necessary: - Ensure any remaining Balancing Energy is deployed. - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available. - When issuing the VDI, the operator should request enough generation to restore frequency and recall approximately 50% of Regulation Up Service. |
| 2 | VERIFY that the Balancing Offset is set to an approximate value that will restore Regulation Service. |
| 3 | IF frequency continues to decay, ENSURE 33% of the TOTAL Responsive Reserve Service is deployed (approximately 760 MW). |
| NOTE: | On depletion of the first 33% of TOTAL Responsive Reserve, ERCOT shall declare an EEA in effect (Protocols Section 6.7.3). |
| 4 | IF Step 3 of this procedure does not arrest the frequency decay AND frequency reaches 59.85, IMPLEMENT EEA 2A and deploy ALL LaaR bid to supply Responsive Reserve. |
| 5 | Follow EEA Procedures as required per section 2.6.6. |
| NOTE: | Verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| NOTE: | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook – ERCOT – TrueTime Frequency |
| 6 | If Regulation Service is temporarily unavailable, AND frequency is below 59.91 Hz and continues to decay, implement the following action as necessary: - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available to recover frequency. - When issuing the VDI, the operator should request enough generation to restore frequency. |
| 7 | When Regulation Service is available, back in service and the frequency is normal, release the Fleet VDI. |

## 2.6.12	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the Back-up Control Center (BCC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC, THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the BCC - Notify them of the situation AND - Have them attempt to make contact with Security at TCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This is ERCOT operator [first and last name], ERCOT is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This is ERCOT operator [first and last name], ERCOT is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support, Telecommunications - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Most potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission/inder Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.7	DC Ties

## 2.7.1	Approve E-Tags for SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Columbus, Ohio is the Tie Operator for the East and North DC Ties. The designation in WebTrans for the East tie is DC_E and the North tie is DC_N. |
| NOTE: | Each time a new or updated E-Tag is submitted, the WebTrans system will automatically validate the E-Tag. WebTrans will display whether the E-Tag has passed or failed validation. The criteria ERCOT uses to validate E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated E-Tag. Currently the only validation criterion set to automatically deny an E-Tag is “QSE Contract”. If this validation fails the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/docs/QSEs.xls Select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. WebTrans Reference Display: Tag Criteria Summary |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: 1.1 Determine if the following information is correct on the E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - “ERCOT-E” or “ERCOT-N” is selected for the correct Point-of-Receipt (POR) or Point of Delivery (POD) portion of the physical path. - “CSWS” is included as a Scheduling Entity on the SWPP TP row in the physical path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the physical path. - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on a quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. 1.2 If one or more E-Tags are submitted that will cause the DC Tie to be overscheduled: - Contact SPP to ensure they also see the over-schedule and they will ensure the appropriate actions are taken to correct the over-schedule. Also inform SPP that if the appropriate actions to correct the over-schedule are not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. - IF an E-Tag is curtailed to zero (0) due to an over-schedule that was not corrected in time, contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. 1.3 Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag was automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve an E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the E-Tag approval timeline, the E-Tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag data to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |

## 2.7.2	Import and Export Limits for the CFE DC Ties

Procedure Purpose: To confirm the import and export limits of the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored Sheet”. |
| 1 | Once the DC-Tie limits for next day are received, check the sum of the E-Tags to ensure the import/export limits are not exceeded on any DC-Tie. If so, contact the PSE of the last E-Tag received and request adjustments to be made. |
| 2 | After midnight, verify that the daily import and export limits have been updated in RTMONI and are displayed correctly on the ERCOT website at: http://mospublic.ercot.com/ercot/jsp/frequency_control.jsp If a discrepancy is found, contact the Transmission & Security Desk to update. |

## 2.7.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. |
| NOTE: | The Railroad DC-Tie has a 15 MW minimum flow requirement. |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: - Determine if the following information is correct on the E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. - Determine if one or more E-Tags being submitted will cause the DC Tie to exceed the import/export limit for the tie. - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the import/export limit for the tie. - Call the PSE to have the E-tag modified, if modification is not done 20 minutes before the start of the ramp then; - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. - Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag was automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor - QSE Summary |
| 2 | The ramp rate for the Railroad DC-Tie will be 50 MW per minute due to reactive issues on the CFE side. Laredo and Eagle Pass DC-Ties will be ramped across a 10 minute window. - Ensure the ramp duration is filled out on Railroad E-Tags only - Laredo and Eagle Pass ramp duration will remain blank Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| 4 | ERCOT will allow QSE’s to submit E-Tags more than one (1) day in advance on the CFE DC-Ties. In these cases there will not be an associated schedule until the day-ahead. If a schedule is not received by 1400 in the day-ahead, notify the QSE and remind them that a schedule is needed. If the schedule is not received by 2000, curtail the E-Tag to zero. |
| 5 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

## 2.7.4	Adjustment of SPP DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-tags.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Periodically refresh the QSE Summary display during the E-Tag adjustment approval window to determine if a QSE has changed an MOI schedule that is now making the E-Tag fail validation. - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E- Tag. - If the E-Tag equals the MOI schedule, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |
| NOTE: | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated Into the Net Scheduled Interchange (NSI) |
| 2 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 2.7.5	Curtailment of SPP DC Ties

Procedure Purpose: The process to curtail E-tags for the SPP DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | When a curtailment alarm is received in WebTrans, - Approve the E-Tag curtailment. WebTrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| 2 | If a QSE or SPP requests an E-Tag be curtailed or adjusted for any reason, curtail the E-Tag to 0 (zero). |
| NOTE: | E-Tag curtailments must be in an “Approved” or “Implemented” status to be calculated Into the Net Scheduled Interchange (NSI) |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

## 2.7.6	Adjustments/Curtailment for the CFE DC Ties

Procedure Purpose: The process to curtail E-tags for the CFE Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. After receiving the import/export limits for next day, it may be necessary to have the PSE adjust E-tags and schedules. |
| NOTE: | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Adjustments are done by the PSE which requires all parties to approve. |
| 1 | If any of the DC-Ties trip, ERCOT will have the responsibility to curtail the E-tags. - Curtail the E-Tags - Ask AEP Corpus to make notification to CFE to approve curtailments |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s) - Re-load curtailed E-Tag(s) - Ask AEP Corpus to make notification to CFE to approve re-loads |
| 3 | Once the import/export limits are posted around 1700, ensure the DC Tie(s) are not overscheduled. If an over schedule is found: - Notify the PSE to adjust the E-Tag(s) using the Last-in-First-Out. If just one PSE is involved they may adjust their E-Tags as they wish. - Notify AEP Corpus with the E-Tag number(s) to approve the adjustment(s) - Ask AEP Corpus to make notification to CFE to approve adjustment(s) |
| 4 | Due to ERCOT transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by the Transmission & Security desk that a curtailment is needed: - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed. - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Ask AEP Corpus to make notification to CFE to approve curtailment(s) |
| 5 | ERCOT must declare an Emergency in order to cut E-Tags without notice. If an Emergency has been declared for a transmission issue and if notified by the Transmission & Security Desk that a curtailment is needed: - Contact AEP Corpus that curtailment(s) will be made and to ramp the appropriate DC-Tie to the needed MW level. - Curtail the appropriate E-tag(s) - Notify AEP Corpus with the E-Tag number that was curtailed - Ask AEP Corpus to make notification to CFE to approve curtailment Typical script to AEP Corpus: This is ERCOT operator [first and last name]. ERCOT will be curtailing E-Tag(s) on the [DC-Tie name] DC-Tie. Please start ramping the Tie to [MW level], the E-Tag will be curtailed shortly. Please repeat this directive back to me. That is correct.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Due to CFE transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by AEP Corpus or the Transmission & Security Desk of CFE’s situation: - Identify if at least 20 – 30 minute notice can be given for curtailment of E-Tag(s), if notice can be given proceeded. If curtailments need to take place immediately, proceeded to Step 7. - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed. - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Ask AEP Corpus to make notification to CFE to approve curtailment |
| 7 | If notified by AEP Corpus or the Transmission & Security Desk of CFE’s emergency situation: - Verify the appropriate DC-Tie is being ramped - Curtail the appropriate E-tag(s) - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Ask AEP Corpus to make notification to CFE to approve curtailment |
| 8 | If CFE does curtail schedules for their transmission issues: - Once curtailment is received from OATI, approve AND - Notify AEP Corpus that they see the curtailment and will ramp the Tie |
| 9 | Once notified that transmission issues are resolved and E-tags can be re-loaded: - Re-load curtailed E-Tag(s) - Ensure AEP Corpus sees the re-loaded E-Tags, AND - Ask AEP Corpus to make notification to CFE to approve re-loads |

## 2.7.7	Managing and Documenting Daily Inadvertent for the SPP DC Ties

Procedure Purpose: To do before-the-fact and after-the fact checkouts for the SPP DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N) or if ERCOT is left off the E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties |
| NOTE: | Due to a deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW out of ERCOT and into SPP, OR - Add MW flow in the direction of the schedule |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

## 2.7.8	Managing and Documenting Daily Inadvertent for the CFE DC Ties

Procedure Purpose: To do before-the-fact and after-the-fact checkouts for the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ROAD_DC, EGPS_DC, or LAR_VFT) or if ERCOT is left off the E-Tag as a Transmission Provider (TP) or Scheduling Entity (SE). |
| CAUTION: | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Corpus Christi TSP for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 5 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, check the bottom box in Column C and click the “Apply Checkout” button. No further action is required. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values: - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change our value to match the DC Tie Operator’s value. Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the CFE DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 2.7.9	Managing Inadvertent Payback

Procedure Purpose: To provide communication contacts and information prior to starting and ending inadvertent payback.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Payback will only be planned when there is room on the DC Tie(s). Power schedules of market participants will supersede any inadvertent payback plan. Payback plans are implemented by the DC Tie Operator. They will bias the DC Tie(s) and create inadvertent in the opposite direction. This will reduce the inadvertent values. |
| NOTE: | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback plan information from the Manager of System Operations or designee |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties - Contact AEP Corpus Christi TO for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Prior to the start of the Payback plan, call the appropriate DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback plan. If payback is planned across the VFT, verify the transmission path (230kV or 138kV). |
| 2 | Periodically check the WebTrans system to ensure that the inadvertent values are decreasing. If they are not decreasing or are increasing, call the DC Tie Operator to determine the reason. WebTrans Reference Display: Daily Inadvertent |
| 3 | Prior to the Payback plan stopping, call the appropriate DC Tie Operator and confirm the agreed upon stop time. |

## 2.7.10	Emergency Energy across the CFE DC Ties

Procedure Purpose: Steps to secure emergency energy across the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must declare an emergency and make the proper posting/hotline call when receiving emergency energy from CFE, whether it is for transmission issues or an EEA situation. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| NOTE: | If there are E-tags that can be curtailed to alleviate the emergency situation, referred to Procedure 2.7.6, Step 5. When notified by Hotline If in EEA situation, export E-tags should be curtailed first before emergency energy is received. |
|  | When notified by Hotline that ERCOT has implemented an EEA level, proceed with this procedure |
| 1 | When ERCOT is in need of the Emergency Energy: When notified by the Transmission & Security Desk of the need for emergency energy for a transmission issue or if in an EEA situation: - If there is import capacity room on the appropriate DC-Tie(s), contact AEP Corpus and request that they contact CFE to see if emergency energy is available - If emergency energy is available, determine the DC-Tie(s), MW amount, time and duration (if possible), - Request AEP Corpus to ramp the appropriate DC-Tie with the emergency energy - Issue AEPSQ4 QSE a VDI for the emergency energy and to AEP Corpus if requested - Forward VDI(s) to Shift Supervisor (fax) as time permits |
| 2 | When CFE is in need of the Emergency Energy: The request will come from either the Transmission & Security Desk or AEP Corpus: - If there is export capacity room on the appropriate DC-Tie(s), coordinated with the Transmission & Security Desk to ensure it will not cause ERCOT transmission issues - With no issues, determine the DC-Tie(s), MW amount, time and duration (if possible) - Coordinate with Operating Period Desk - Issue AEPSQ4 QSE a VDI for the emergency energy and to AEP Corpus if requested - Notify AEP Corpus to ramp DC-Tie(s) - Forward VDI(s) to Shift Supervisor (fax) as time permits |

## 2.7.11	EEA 1 Schedule across the SPP DC Ties for EEA 1

Procedure Purpose: Steps to secure a schedule across the SPP DC tie(s) in an Energy Emergency Alert 1.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Once notified by Hotline, the DC-Tie Operator at the back-up is responsible for carrying out this procedure. |
| 1 | Notify the SPP Reliability Coordinator of ERCOT’s EEA 1 status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. We will contact the Tariff desk to inquire about the availability of transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2A, 2B, or 3, proceed to Section 2.7.12 If there is transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the transmission service available. Thank you.” |
| NOTE: | SPP will contact PSEs with unscheduled reservations and notify them of ERCOT’s EEA 1 status. PSEs may choose to use their reservation to schedule into ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers): Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-Tag(s) and proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify the DC Tie Operator of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag (s) for an EEA 1 schedule. |

## 2.7.12	Emergency Energy Request across the SPP DC Ties for EEA 2A, 2B or 3

Procedure Purpose: Steps to secure emergency energy across the SPP DC tie(s) in an Energy Emergency Alert 2A, 2B or 3.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE: | If ERCOT goes directly to an EEA 2A, 2B or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below. |
| 1 | Notify the SPP Reliability Coordinator or ERCOT’s EEA status Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will contact the Tariff desk to inquire about the availability of emergency transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the emergency transmission service available. Thank you.” |
| NOTE: | ERCOT must have the Reliability Coordinator Information System (RCIS) updated with the EEA 2 or 3 status before SPP grants emergency transmission service. |
| NOTE: | SPP will curtail all non-firm transmission service schedules going out of ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-Tag(s). Proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status: Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| NOTE: | Keep SPP informed of ERCOT’s status. |

## 2.7.14	Fast Start Emergency Schedules to Southwest Power Pool (SPP)

Procedure Purpose: Steps to provide emergency assistance to South West Power Poll across the SPP DC ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Every effort should be made to render assistance during emergency conditions. SPP will notify ERCOT that emergency assistance is needed. |
| 1 | VERIFY that providing emergency assistance to SPP will not put ERCOT in an insecure state, or worsen an existing insecure state. |
| NOTE: | SPP will contact the DC Tie Operator and arrange to maximize the DC tie output into SPP. It is not necessary to confirm that an emergency condition has been posted in the Reliability Coordinator Information System (RCIS). SPP may need to act before the RCIS is updated. |
| 2 | Notify the Operating Period Desk to adjust the Offset to minimize the use of Regulation. |
| 3 | When possible: - Contact AEP QSE and instruct them to create and submit an E-Tag for the emergency assistance (this can be done after-the-fact but within an hour of the event). - Issue a VDI to AEP QSE for the emergency assistance. |

## 2.8	Outages

## 2.8.1	Maintenance Level 2 & 3 Outages

Procedure Purpose: Process level 2 and 3 maintenance outages in the Outage Scheduler.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Maintenance Level 2 and 3 outages are coordinated with the ERCOT Outage Coordination Group. These outages should not be “accepted” by anyone other than that group. However, until they are accepted in the Outage Scheduler, they will continue to show up every time the Outage Scheduler refreshes (that is about every two minutes). |
| 1 | DO NOT check the “accept” box for Maintenance Level 2 and 3 Outages in the Outage Scheduler. Instead, place those Maintenance Level 2 and 3 outages in “Study” status and notify the Outage Coordination group of the Maintenance Level 2 or 3 Outage, by email to “OPS Outage Coordination” distribution list. |