## Power Operations Bulletin # 406

ERCOT has revised the Shift Supervisor Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

1.3.5	Three-Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been place throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |

## 2.1.6	Notification of a Protective Relay or Equipment Failure Report

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | PRC-001-1 |  |  |  |
|  | R2.2 |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC: | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| 1 | Notify the shift engineer or the on-call engineer as soon as possible when notified that a protective relay or equipment failure reduces system reliability and there is no back-up protective relay available. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - OPS Planning - Shift Supervisors - The subject line of the e-mail should read “Protective Relay or Equipment Failure.” - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | The TO or QSE may e-mail a “Mis-Operation Relay form”, forward to the above identified e-mail address. |
| 4 | Log information available in the Log as time permits. |

## 2.1.12	Monitoring CSC & W-N Stability Limits

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-004-0 |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC | “Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies” |
| 1 | Monitor CSCs and the W-N stability limit during the shift. If necessary: - Open PI Process Book - Select Transmission Limit & Flow Summary for the ERCOT Top Page tab. - Check each CSC flow during the desired date range - Select Calendar to change the date range (The display will graph the CSC limit and line flow for that date range) - Deselect first flow and check next flow - Continue until all flows have been selected and all data has been collected. |
| 2 | If any CSC exceeds the limit for more than 30 consecutive minutes: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. - Save the study in the STNET directory. If the W-N stability limit or N-H VSAT limit is exceeded for more than 30 consecutive minutes, notify the Manager, System Operations immediately. |
| 3 | Notify by e-mail (including data from Step 2) - Shift Supervisors - Ops Support Engineering - Isabel Flores |

## 2.2.1	Supervise Response to System Disturbances

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 |  |  |  |
|  | R6 |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC: | Balancing Authority shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. Contingency Reserves must be restored within 90 minutes. The restoration period begins at the end of the disturbance recovery period. |
| 1 | IF the system disturbance cannot be normalized with current on-shift staff, THEN IDENTIFY and ASSIGN additional System Operators, Operations Support, Operations Planning, or Market Operations staff to assist in normalizing the system condition. |
| 2 | The ERCOT Shift Supervisor will ACT as the main contact and answer inquiries between the control room and other ERCOT operations groups during system disturbances. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Section 2 of the Desktop Reference Guide: Emergency Communication/Notification Guidelines. |
| NOTE: | See Phone Book at Shift Supervisor’s Desk. |

## 2.2.5	Gas Restriction Notifications

Procedure Purpose

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Once notified by a QSE of gas restrictions, send an e-mail to: - Gas Company Notifications This will notify all appropriate ERCOT staff. |
| 2 | Ensure gas restriction will not cause ERCOT reliability issues. Follow the necessary procedures. See 2.2.11 for additional information if needed. |

## 2.2.8	Texas RE Event Analysis

Procedure Purpose

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | WHEN a significant event (see NOTE: below) occurs, within one hour - Complete the form located in Section 2 of the Desktop Reference Guide: “Texas RE Event Analysis Form” - E-mail to distribution group entitled “TRE Event.” - The subject line of the e-mail should read “TRE Event.” |
| NOTE: | For purposes of this event analysis process, significant events include, but are not limited to, the following: - Energy Emergency Alert (EEA) implementation - Emergency Notice issued - Deployment of LaaRs - Simultaneous loss of any combination of three generating units, transmission lines, and autotransformers (138 kV and above) - Special Protection System (SPS) activation - Remedial Action Plan (RAP) or Mitigation Plan (MP) implementation requiring load shedding - Under frequency relay operations (or frequency deviations greater than 0.3 Hz from scheduled frequency) - Sustained voltage deviations greater than 5% on 345 kV system - First contingency security violations for significant transmission elements - Failure of computer systems at ERCOT, QSE, or TO (failover to backup systems is not a reportable event) - Voltage collapse on portions of 138 kV or 345 kV system - Loss of an ERCOT, QSE, or TO control center - Black Start Plan initiation - Uncontrollable loss of 150 MW or more of firm load shed for more than 15 minutes from a single incident - ERCOT failure to meet NERC Performance Standards related to frequency control or transmission security |
| NOTE: | There are also DOE and several NERC reportable events that could trigger an investigation. To report such an event, see section 2.2.9. |

## 2.2.9	NERC and DOE Disturbance Reporting

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-004-1 | DOE OE-417 |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
|  | When Disturbance reporting is required: |
| NOTE: | NERC E-mail address: esisac@nerc.com, fax (609) 452-9550 DOE E-mail address: doehqeoc@oem.doe.gov, fax (202) 586-8485 DOE Operation Center voice phone: (202) 586-8100 |
| NOTE: | Disturbance Reporting requirements can be found in NERC Reliability Standard EOP-004-1. The DOE OE-417 Schedule 1 report and NERC Preliminary report are to be filed within 1 hour after the start of the incident or disturbance. The Operations Support Engineering group will follow-up with the DOE OE-417 Schedule 2 report and NERC Final report. |
| 1 | Forward the TSP(s) report or the Director of Security’s report to NERC, DOE, and the “NERC and DOE Disturbance Reporting” e-mail list. Ensure all three entities receive the report. (e.g. If TSP or Director, Cyber Security sends a report to only one entity; make sure the other two entities receive the report as well.) |
| 2 | ERCOT is required to issue a report to NERC and DOE even when the disturbance does not require a report from a TSP (e.g. The disturbance involves two or more TSP areas that meets the requirements for reporting.) or if a report is received from the Director, Cyber Security, then do the following: - Complete required NERC report per Attachment 1-EOP-004 and/or - Complete required DOE OE-417 Schedule 1 report - Forward reports to NERC, DOE, and the internal ERCOT “NERC and DOE Disturbance Reporting” e-mail list. - esisac@nerc.com - doehqeoc@oem.doe.gov - NERC and DOE Disturbance Reporting |
| 3 | In the body of the e-mail, type the following: "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release." |
| NOTE: | NERC report forms can be downloaded at http://www.nerc.com/page.php?cid=5¦66 DOE OE-417 report forms can be downloaded at ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc |
| NOTE: | A guideline on “Threat and Incident Reporting” can be found at http://www.esisac.com/ |

## 2.2.10		PUC Daily Report

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The PUC reports are to be generated twice per day: In winter months at 0100 and 0500 In summer months at 1100 and 1500 The timing change will be determined by the Manager, System Operations. |
| NOTE: | Be able to provide a list of unplanned generation outages for the day if requested by the PUC. |
| 1 | Complete the PUCT Daily Report template at the appropriate times. E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Do not add editorial comments to this report that reveal market sensitive data. General comments that convey overall system conditions are allowed. |
|  | Revise the last report sent and resend it if: - The probability of an EEA event increases. Give reason(s) for escalation, OR - Conditions change that required new notices to be issued or cancelled, such as, an OCN , Advisory, Watch, or Emergency Notice OR - A shortage of generation capacity develops OR - Local reliability concerns arise which include actual overloads and/or loss of load, especially the Laredo area, OR - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if there are unplanned outages of the generation units in the area. - Localized gas restrictions, not expected to cause reliability issues. - DCS event occurs - “ERCOT only” NERC and/or DOE event occurs. These events are market sensitive so provide a brief description without the market sensitive information. |
| 2 | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves. - Medium - A Watch is in effect for Adjusted Responsive Reserves and/or - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves and/or - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Adjusted Responsive Reserves and trending downward after procuring quick-start capacity and/or - Excel MAI shows multiple hours of insufficient reserves and ERCOT has been unable to correct the capacity insufficiency over several hours and ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect |
|  | Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect |
| 3 | Potential for EEA Level 2B - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical EEA Level 2B in effect |
| 4 | Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B (if available) in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |
| NOTE: | When conditions have returned to normal, update report and e-mail. |

## 2.2.14		EEA (Energy Emergency Alert) Reporting

Procedure Purpose

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-002-2 | IRO-014-1 |  |  |
|  |  | R1.1.2 |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | There are four levels of EEA’s, as ERCOT enters each level; postings must be made on the NERC Reliability Coordinator Information System (RCIS). EEA 0: All previous Watches have been terminated and the entity can supply all energy requirements. EEA 1 – All available resources in use. The entity foresees or is experiencing conditions where all available resources are committed to meet firm load, AND is concerned about maintaining its required Operating Reserves. EEA 2 - Load management procedures in effect. The entity can no longer provide expected energy requirements and foresees or has implemented procedures up to, but excluding, shedding firm load. EEA 2 is comparable to EEA 2A and EEA 2B. EEA 3 – Firm load interruption imminent or in progress. The entity foresees or has implemented firm load shed. You may declare whatever alert level is necessary, and need not proceed through the alerts sequentially. Reference NERC Reliability Standard EOP-002-2 Capacity and Energy Emergencies for detailed information. http://www.nerc.com/files/EOP-002-2.pdf |
| 1 | If EEA Level 1 is implemented, post following message to RCIS: “ERCOT is in EEA 1.” |
| 2 | If EEA Level 2A or Level 2B is implemented, post following message to RCIS: “ERCOT is in EEA 2.” |
| 3 | If EEA Level 3 is implemented, post following message to RCIS: “ERCOT is in EEA 3.” |
| 4 | When recalling EEA, reverse the order and make the appropriate RCIS postings. When the emergency condition has been terminated, post EEA 0 (zero), as shown below: “ERCOT is in EEA 0.” |
| NOTE: | Progression to EEA Level 3 requires filing a report with NERC. The report (Energy Emergency Alert 3 Report) can be obtained from the following link: http://www.nerc.com/fileUploads/File/Energy_Emergency_Alerts/Energy_Emergency _Alert_3_Report_Form.doc |
| NOTE: | Refer to Section 2 of the Desktop Reference Guide: ERCOT/NERC EEA Notification Requirements. |

## 2.5.1	Prepare Daily Grid Operations Report

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Daily Grid Operations report is in a web base application, which is intended to create a report for the Public Utility Commission and Market Participants on a daily basis. |
| 1 | Section 1: Index Enter the Peak Load, Time of Peak Load, Planned Peak Load (from the day ahead plan from the Day Ahead desk), and time of planned peak |
| 2 | Section 2: Constraints Encountered During the Day For each constraint activated in RTCA a record should be placed in this section. DO NOT PLACE REPEATED ENTRIES FOR REPEATED STARTS AND STOPS OF CONSTRAINTS DURING THE DAY UNLESS IT IS AN OC1. All OC1’s must be entered each time the constraint is activated. All OC1’s must also have the contingency and overloaded element listed. VDI’s and OOME instructions should also be entered in this section as follows. Time: Interval Ending Constraint: A brief name of the constraint, or For OOME a statement of what was OOM’d and what direction (up or down) Examples: Jewett - TH Wharton OC3; OOME XXXX up or down Reason: A description of what element or limit was loaded, what the loading and percentage was when the action was taken, and what the limit was when taken. Example: Loss of Jewett -TH Wharton and Tomball 345KV overloads Watson Chapel - Robertson 138KV - 110% of 105 MVA rating. |
| 3 | Section 3: Other Notable Events A description of any OCN’s, Watches, Advisories, and Emergency notices issued to the market. A description of any frequency deviations over .1 hertz including unit trips. A description of any market extensions or delays or equipment failures affecting ERCOT’s ability to deploy services or control the system. |

## 2.7.7	Monthly Testing of Satellite Phone System

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, test the Satellite Phone System with Transmission Operators to determine whether or not ERCOT has communication capability via the Satellite Phone System. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in Section 7 of the Desktop Reference Guide for instructions on how to place a satellite phone call. |
| 2 | - Call each Transmission Service Provider using the preprogrammed number on the Turret Phone. Refer to page #2 of the ERCOT Satellite Phone User Guide for instructions. If there is no answer: Call the Transmission Service Provider directly using the Satellite Phone number provided in Section 7 of the Desktop Reference Guide. - As contact is made with each Black Start Transmission Service Provider, (as listed in Section 7 of the Desktop Reference Guide) establish a time when a Satellite Conference Bridge Call will be made from the appropriate ERCOT Operations Desk. - Refer to Section 7 of the Desktop Reference Guide for a list of Transmission Operators, Satellite phone numbers and Moderator Pass Codes for each ERCOT Operations Desk. |
| 3 | When testing is completed by all desks, fill out Monthly Satellite Testing forms located in P:\ SYSTEM OPERATIONS “Satellite Testing Phone Testing Forms” folder. |
| 4 | File a hard copy in the control room. |
| 5 | Log the test date and results in the Shift Supervisors Operations Log. |
| NOTE: | - Send the compiled results of the Satellite phone test by e-mail to: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |
| NOTE: | Not all Transmission Operators have satellite phones, so the call will be coming in on their regular landlines. You may verify whether or not they are communicating via satellite phone or regular landlines while testing. |

## 2.8.5	Review New Communications from the Manager, System Operations or Designee

Procedure Purpose:

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: May 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Periodically, the ERCOT Manager, System Operations will issue new operating instructions, operating memos, and other relevant communications to all System Operators. These types of communications are used to clarify or temporarily modify existing procedures. - The Shift Supervisor is required to review these communications to ensure that the new instructions are known and understood by all desks in the shift. This task is especially crucial when returning from vacation periods, or several rest days. This review of Manager, System Operations issued communications includes verification of e-mail and hardcopy communications or instructions. Clarification of new instructions, if needed, must be addressed directly to the Manager, System Operations. |
| 1 | - REVIEW all communications received from the Manager, System Operations including e-mails, letters, and memorandums. |
| 2 | - DETERMINE if new or revised operating instructions and operating memos were issued since the last verification of communications was made. |
| 3 | - IF new or revised operating instructions and operating memos were issued, VERIFY which system operator positions and operating procedures may be affected. |
| 4 | - VERIFY that the operators on the affected desks are aware and understand the new or revised operating instructions, and operating memos. |
| 5 | - IF clarifications are needed, REQUEST clarification from the Manager, System Operations. |