Power Operations Bulletin # 409

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.1.2	Real Time Contingency Analysis (RTCA) Constraint Validation

Procedure Purpose: To run RTCA.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. |
| NOTE: | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Energy Management System (EMS) and an electronic copy is located on the ERCOT website under ‘Grid Information’ in the Transmission section. http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA) in the key document section. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 20 minutes. |
| 3 | If RTCA has not run within 20 minutes, refer to “RTCA Call Out Procedure” in section 2.1.3. |
| 4 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist, - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are located in the daily Outage Notes. |
| 4a | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or -4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take the DIRECT appropriate voltage control action. |
| 5 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 6 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Desk Top Guide Section 3.6 for guidance. |
| 7 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 8 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 9 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 10 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Take additional manual actions as necessary to resolve the contingency overload within 30 minutes. Notify the on-call Operations Support Engineer and ask for a Mitigation Plan if one does not exist. If the system operator determines that the Pre-contingency value or system topology is incorrect, OR if a SPS, RAP, PCAP, TOAP, or MP exists, step 10 may be omitted. |
| 11 | If congestion management techniques fail to resolve congestion and the transmission system is beyond first contingency criteria, ISSUE a Watch per section 2.5.3. |
| 12 | Periodically check the Base Case violations display for Thermal overloads. A “thermal overload in real-time” means loading above 100 % of the NORM/Continuous rating. |
| 13 | If a valid Thermal overload exists in real-time, EMPLOY congestion management techniques to relieve the overload. System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit violations. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 14 | Periodically check the “Contingency Solution Results” display. If there are unsolved contingencies, run the State Estimator again. If unsolved contingencies remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. If there are known reasons that the contingency is unsolved, as time permits, notify the on-call Operations Support Engineer to verify system conditions have not changed.. |

# 2.1.4	OOME – VDI Guidelines

Procedure Purpose: To provide guidelines for OOMEs and VDIs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 1 does not apply to wind units. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOME’d off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, coordinate with the Frequency Operator for issuance of VDI to relieve the QSE from their Ancillary obligation if necessary. - Issue an instruction to release the QSE from the dispatch instruction so they can come back into compliance. |
| 5 | When an SPS activates and that SPS activation de-rates a resource or takes a resource off line, issue a VDI to the affected QSE. - The beginning time on the VDI will be the interval that the SPS activated. - The ending time on the VDI will be the interval the SPS was restored to service. - The exception will be VDI’s will not exceed four (4) hours after the time of activation. - If the resource is a DC tie, include the name and zone of the tie. Typical Script on the VDI: “SPS activation, caused <unit name or DC tie name> to <trip or runback>”. |
| 6 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with a Settlements only VDI stating “OOMC for Quick-start” on the VDI form. |
| 7 | As time permits, forward the VDI to the Shift Supervisor |

# 2.1.5	Three Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been place throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |

# 2.1.6	Monitoring Priority Outages in Real Time Monitor Mode

Procedure Purpose: To monitor priority outages in real time.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | A priority outage is one that affects generation. |
| 1 | Select the required outage or outages in the Outage Scheduler to be monitored in the Real-Time Monitor. |
| 2 | Select the “Toggle Monitor Flag” from the drop down and Apply. |
| 3 | Select switch to the Real-Time Monitor to view the monitored outage or outages. |
| 4 | Verify that the outage is being monitored by change in color to pink. |
| 5 | Monitor outages as required. |
| 6 | When a priority outage returns to service ensure the generation that was being dispatched is released. |
| 7 | Log any issues as time permits |

# 2.2 	Manage Transmission Congestion

# 2.2.1 	Real Time Constraint Activity Manager (RTCAM) Congestion Management

Procedure Purpose: To alleviate congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Local Congestion Management Techniques consist of OC3s, Unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| NOTE: | Phase shifters could at times be used to help with congesting management: - Putnam – NW/WN transfers to increase CSC transfer capability - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |
| 1 | VERIFY SFT is enabled in the MOI. - This can be determined by making sure that the check box next to “Run SFT for Real-Time Markets” on the Real-Time Balancing Market display is checked. If it is not checked, then check it. |
| 2 | DETERMINE if RTNET and RTCA has solved within 20 minutes. |
| 3 | If RTNET and RTCA have not solved within 20 minutes, refer to the “RTCA Call Out Procedure” in Section 2.1.3 |
| 4 | DETERMINE if RTNET has solved with a solution status of “VALID SOLUTION – NO SFT CASE.” - If RTNET has this solution, notify the State Estimator On-Call Engineer. |
| 5 | If RTCA has solved within 20 minutes, EXAMINE the RTCAM Branch Violations and Operating Constraints List. |
| 6 | EXAMINE the constraints with the “Active” check box filled in. - VERIFY that an OC3 is created for all overloaded active constraints in the MOI by selecting the “constraint” tab from the “Real-Time Balancing Market” screen in the MOI. In the Type column, sort descending. All OC3s will be sorted to the top of the page. - If an overloaded constraint is active in RTCAM, but the corresponding OC3 is missing from the MOI, LOWER the value in the “% Rating” column in RTCAM to tighten the constraint until the OC3 appears in the MOI. - If an OC3 is active in the MOI, but the corresponding constraint in RTCAM is well below the monitored rating, INCREASE the value in the “% Rating” column in RTCAM to loosen the constraint. |
| 7 | When an OC3 deploys quick start units for congestion, do one of the following: - Issue an “OOMC VDI” for settlements on the quick start unit(s) that are required to mitigate congestion - Issue an OOME for quick start unit(s) using the OOM tool and keep the OC3 active, or - Use OOM tool to OOME for quick start unit(s) instead of activating an OC3, or - Issue a VDI to disregard the unit specific deployment and write “instructed deviation” on the VDI if congestion can be resolved without unit(s) OOMC VDI for quick start units will only be given under the local congestion scenario, balancing and zonal deployments are not included. Follow up with a Settlements only VDI stating “OOMC for Quick-start” on the VDI form. |
| 8 | To activate a constraint, check the “Active” check box next to the constraint to be activated. The text in this row of data will change to red and it will be immediately sorted to the top of the display. |
| 9 | To deactivate a constraint, uncheck the “Active” check box next to the constraint. Uncheck the “Retain” check box as well, if desired. Leaving the “Retain” box checked will only cause the constraint to remain on the Operating Constraints List display when an overload is not occurring. |
| 10 | To acknowledge constraints that are determined to be erroneous or are already accounted for, check the check box in the “Ack.” Column. This will sort the constraint to the bottom of the display. |
| 11 | Special Protection Schemes (SPS), Remedial Action Plans (RAP), and Pre-Contingency Action Plan (PCAP) analysis - EXAMINE the results in RTCAM for RAP or SPS activation, using the “SPS” and “RAP” columns on the Operating Constraints List display. - If “SPS” and/or “RAP” is checked, EXAMINE the color of the background. Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. - ADJUST initial “% Rating” higher if activating a constraint for a post-RAP/SPS overload if needed. This is because RTCAM/SFT can not model RAP/SPS when generating OC3 constraints so they tend to over-constrain at 100 % of rating. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |

# 2.2.3 	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: Processes to relieve local congestion surrounding the CFE DC-Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. |
| NOTE: | ERCOT may adjust generation to solve local congestion in the areas of the CFE DC-Ties; however OOMC’s will not be utilized to allow schedules to flow. |
| NOTE: | When curtailing E-tags for transmission issues, they should only be curtailed for a couple hours at a time, hourly if possible. |
| 1 | Update RTMONI with the CFE DC-Tie Limits each night across midnight. |
| 2 | If E-Tags must be curtailed to control post-contingency overloads: - Contact the ERCOT DC-Tie Operator to have the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 3 | If E-Tags must be curtailed to control the Valley or Laredo Import: - Contact the ERCOT DC-Tie Operator once the Valley or Laredo Import is at 90% and will continue to climb. - Request to have the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 4 | If curtailments are being made, keep RTMONI updated with new limits. |
| 5 | As room becomes available, keep the ERCOT DC-Tie Operator notified so E-tags can be re-loaded |
| 5 | ERCOT must declare a Transmission Watch or Emergency in order to curtail E-Tags immediately. If a Watch or Emergency has been declared for a transmission issue: - Contact ERCOT DC-Tie Operator to have the appropriate DC-Tie ramped to needed MW level - Ensure the Transmission Watch or Emergency has been posted on the ENS and MIS - Notify the Shift Supervisor |
| 6 | ERCOT will curtail E-Tags for CFE for their transmission issues or emergencies. If contacted by AEP Corpus of a CFE issue: - Identify if at least 20 – 30 minute notice can be given for curtailment - Notify ERCOT DC-Tie Operator with information to make curtailment - Notify the Shift Supervisor |

# 2.2.4 	Zonal (CSC) Congestion Management

Procedure Purpose: To relieve zonal congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTES: | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. The CSC Limits are computed and posted on the ERCOT website by Operation Support Engineering during the day-ahead planning process. These limits are based on the day-ahead Resource Plans and forecasted system conditions. Potential IROLs are defined in the day-ahead analyses or when changes in system conditions warrant further evaluation. If a CSC has been marked as an IROL on the “Transmission Limits” sheet, ensure the limit is honored. If the limit is exceeded, take all possible actions to get below the limit in 30 minutes or less. An OC1 should only be utilized for a zonal overload where both the contingency and the overloaded element include a CSC and/or CRE. A current list of CSC/CRE DATA is posted on the following ERCOT website: http://mospublic.ercot.com/ercot/jsp/csc_cre.jsp |
| 1 | Monitor and update the RTMONI limit page at least once an hour. The number should be rounded to a whole number. |
| 2 | When the CSC actual flow approaches or exceeds the limit from the “Real-Time CSC Limit Calculator”, Activate the OC1 |
| 3 | When RTCA shows a post contingency zonal overload and the CSC has not exceeded its’ limit on the “Real-Time CSC Limit Calculator, AND RTCA has solved within the last 10 minutes, then RTCA results should be used as a basis for managing zonal congestion, activate the OC1. When the zonal overload has been resolved, restart the Real-Time CSC Limit Calculator for a new CSC limit. |
| 4 | If RTCA shows a post contingency zonal overload and the Real-Time CSC Limit Calculator has run, the application will display the letters OL (Over Limit). Once the zonal overload has cleared in RTCA, restart the Real-Time CSC Limit Calculator application by activating the manual Run Sequence on RTCA. |
| 5 | If the Real-Time CSC Limit Calculator has run and the application does not display a limit and the element displays “Basecase overload”, “Temporarily Unavailable” or “Min West”; the previously published value will remain the same unless RTCA indicates a thermal or post contingent overload. |
| 6 | In the event the Real-Time CSC Limit Calculator is inoperable. Post the limits from “Transmission Limits to be Monitored” daily report to RTMONI. If RTCA shows a post contingency overload before we get to the posted CSC limit start controlling to RTCA and post limit in RTMONI. If you have reached the CSC limit and it hasn’t come in on RTCA, keep raising the posted limit until the new limit is defined by the RTCA results, then post it in RTMONI and start controlling to the new CSC limit. |
| 7 | The W-N and N-W OC1 should not be used for a contingency overload through the Putnam 138KV line UNLESS the Putnam Phase-Shifter is out of service. If an overload on the Putnam 138kV lines shows in RTCA, have AEP adjust the phase-shifter set point lower to clear the overload. |
| 8 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques: - OOME/VDI resource down - Post a message on the MIS: Typical Script: “Zonal congestion management techniques have been unsuccessful in controlling the “[zone – zone]” CSC congestion. Local techniques will also be utilized.” |
| NOTE: | If Zonal Management Techniques failed to control Zonal Congestion and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |
| 9 | A PCAP exists to manage North – South congestion by opening the 138kV line between Goldthwaite and Brownwood. The following reliability actions should be taken: - Activate the North – South OC1 - Run a real-time snapshot study to determine if the PCAP works - The PCAP will cause local congestion, determine if enough generation can be moved to resolve the congestion. - If so, activate the OC3 and deactivate the OC1 - If not, keep the OC1 activated |
| 10 | If Local Techniques fail to control a non zonal post contingency overload involving CSC/CRE elements within 30 minutes, utilize Zonal Congestion Management Techniques. - A transmission condition has been identified causing unreliable operation or overloaded elements. - An Emergency Notice must be declared by ERCOT before Zonal Techniques may be utilized - Post a message on the MIS Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to help control the [zone – zone] CSC” |
| NOTE: | Zonal limits may change due to an outage cancellation, extension of an outage, or the early completion of an outage. |

# 2.2.5 	West North Dynamic Stability Limit

Procedure Purpose: To maintain West to North stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | If the West-North Stability limit calculated on the spreadsheet changes value or color, update the RTMONI limit on the “Stability-WN” monitor to the value shown on the spreadsheet. |
| 2 | If the monitored flow on the Stability-WN monitor is approaching 85% and wind is climbing: - Activate the West – North OC1 - Change the W-N CSC limit to the Stability limit in RTMONI to give transparency to the Market. - Post a message on the MIS: Typical Script: “ERCOT is controlling the West - North Dynamic Stability Limit with the West – North OC1”. |
| 3 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - OOME/VDI wind down - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control the West to North dynamic stability limit.” |
| NOTE: | With the passing of PRR 773, Protocol 4.10.4.1 now requires LSL be set at 10% of the name plate rating of the WGR. |
| 4 | If Wind Generation Resources in the McCamey Area are utilized follow procedure: 2.2.12 Managing Wind Powered Generation Resources (WPGR) in McCamey Area. |
| NOTE: | If Zonal Techniques failed to control the West-North Stability limit and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |

# 2.2.6 	North-Houston Dynamic Stability Limit

Procedure Purpose: To maintain North to Houston stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | VSAT should be checked at least every hour, or more frequently as necessary. If North-Houston 345kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. |
| 2 | Determine if the Reliability margin is within 200MW of the Reliability margin: - N-H G – 400 MW - N-H L – 400 MW If the value is within 200MW of the Reliability margin: - Request TSP’s in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| 3 | Determine if the Reliability margin is at or below the Reliability margin: - N-H G – 200 MW - N-H L – 200 MW If limit value is at or below the Reliability margin: - Activate the North – Houston OC1 - Change the North – Houston CSC limit in RTMONI to the N-H VSAT Transfer Limit located in VSAT for Market transparency. - Post a message on the MIS: Typical Script: “ERCOT is controlling the North - Houston dynamic stability limit with the North – Houston OC1”. |
| 4 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - Fleet up in Houston area - Utilize quick start units in the Houston area - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control North – Houston dynamic stability limit.” |

# 2.2.7 	OC1 Limits for Outage Support

Procedure Purpose: Adjusting OC1 limits to support an outage.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Adjust OC1 limits as required to support an outage. - If flow across a CSC is already below the limit required to support an outage, then it is permissible to wait and adjust the OC1 limit at the scheduled start time of the outage. - IF flow across a CSC is above the limit required to support an outage, then adjust the OC1 limits for intervals preceding the scheduled outage start time such that flow across the constraint is gradually reduced to at or below the limit required to support the specific outage. - While this action might result in over-constraining for a brief period, it is preferable to the negative effects of a sudden reduction in the OC1 limit. |
| NOTE: | If step 1.2 is required, use the MIS and post that ERCOT is controlling to a limit other than the one posted. Typical Script: The “CSC Name” limit will change to “MW Amount” at “Time”. ERCOT will start controlling to this limit in accordance with Section 2.2.4 of the Transmission Security Desk procedures. |
| 2 | When a CSC limit changes, immediately change the limit in RTMONI. Record this event in the Transmission Security log. |

# 2.2.11 	Mitigation Plans

Procedure Purpose: To implement a Mitigation Plan.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. If necessary, continue to use congestion management methods for post contingency loading after initiating the MP. With a MP, an operator does not need to declare a Watch for a post contingency overload. If a MP is enacted and subsequent congestion management techniques do not control post contingency loading, ISSUE a transmission Watch. |
| CAUTION: | MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. |
| 1 | When RTCA shows a post-contingency overload greater than 100% of the Emergency Rating, attempt to resolve the overload by using congestion management methods. |
| 2 | If congestion management methods do not work, review the MPs to determine if an action plan exists for this overload condition. |
| 3 | If a MP exists If a MP exists for this contingency: - Review the Mitigation Plan with the associated Transmission Operator - [TO] repeats back directive to verify the plan is understood. - Notify the Shift Supervisor of the anticipated actions. |
| 4 | IF a MP does not exist for this contingency and the Outage Notes do not provide a plan, REQUEST (as time permits) that Operations Engineering investigate development of a MP. |
| 5 | If the contingency anticipated by the MP takes place: - DIRECT implementation of the MP to the Transmission Operator - [TO] repeats back directive to verify implementation is understood. - RESPOND as quickly as possible to requests made by the Transmission Operator in accordance with the MP If necessary, continue to use congestion management methods for post contingency loading after initiating the MP. |
| 6 | When the contingency clears, notify the TO as soon as possible. |

# 2.2.14 	Post Contingency Overload of the Sandow Autotransformer

Procedure Purpose: To relieve the post contingency overload of the Sandow autotransformer in the event that Sandow unit # 4 trips of line. OR If Sandow unit # 4 is off line and the Sandow auto transformer is overloaded.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | Implement the appropriate action: - IF LaaR are available at Sandow, issue an OOME VDI to the Luminant QSE to deploy the MW amount of LaaR necessary to relieve the overload; up to the amount of LaaR scheduled by Luminant. - IF LaaR are not available at Sandow, instruct the ONCOR TSP to shed <amount> MW firm load in the MW amount necessary to relieve the overload. |
| 2 | IF LaaR were deployed in Step 1 AND the overload duration is expected to exceed 90 minutes, instruct the Luminant QSE to replace their RRS obligation from another source. |
| NOTE: | If needed, work with the TSP/ appropriate entity if they request to rotate the deployed LaaR/firm load that was shed. |
| 3 | When the overload has been resolved AND system conditions permit, implement the appropriate action: - IF LaaR were deployed in Step 1, terminate the OOME VDI with the Luminant QSE. IF firm load was shed in Step 1, instruct the ONCOR TSP to restore <amount> MW of firm load at Sandow. |

# 2.3.5 	Interrupted Outages

Procedure Purpose: Process to restore an outage due to adverse weather conditions.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Use this process when a continuous outage needs to be restored for a day due to adverse weather. |
| 1 | CHANGE the start time in the Outage Scheduler to the new start time. |
| 2 | Log in the Transmission log: - The name of the Transmission Operator requestor - The original Start Date of their outage - The reason |
| EXAMPLE: | A continuous outage scheduled from 0800 Tuesday 3/30/09 until 1600 Monday 04/06/09. The Transmission Operator started the outage Tuesday and bad weather has moved in during the day. The Transmission Operator reports they will close the line, but would like to resume work Wednesday 0800 04/01/09 change the planned start time to 0800 on 04/01/09. The end date cannot be extended beyond the original approved end time. |

# 2.4.3 	Voltage Security Assessment Tool (VSAT)

Procedure Purpose: To monitor system conditions and prevent voltage collapse.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure 2.2.6 North-Houston Dynamic Stability Limit. |
| NOTE: | VSAT should be checked at least every hour, or more frequently as necessary. |
| NOTE: | To contact VSAT support, check the board in the back of TCC for the on-call personnel. |
| 1 | Determine if VSAT has run in the last 80 minutes. Reference Display: Network Online Sequence - If VSAT has not run in the last 80 minutes, contact VSAT support. - IF a South-Houston or North-Houston 345 kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. Otherwise, continue with following steps. - If any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below, it is suggested to manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) more frequently than the periodic scheduled VSAT run and proceed to step 2. Otherwise, continue with the following steps. Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. |
| 2 | Confirm that VSAT is indicating either “Normal” or “Pending” status. NOTE: If VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status, contact VSAT support. Reference Display: Network Online Sequence |
| 3 | With VSAT in “Normal” status, determine if it indicates that a Reliability Margin may be exceeded. Reference Display: VSAT Results Page |
| NOTE: | If one of the Comanche Peak units is forced or planned to be offline, there must be at least two sizeable DFW area units online at all times (along with the one Comanche Peak unit online). |
| NOTE: | If VSAT does not indicate a Reliability Margin is below the Reliability Margin, no further action is required. |
| 4 | Determine if the Reliability margin is less than the value located in the table below. Reference Display: Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200Mw. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. If the VSAT Reliability margin value is less than the Reliability margin value posted: |
| 5 | Check to see if the same contingency is unsolved in RTCA. Reference Display: Contingency Analyst Solution Results If so, call VSAT support and proceed to Step 7. If not, call VSAT Support for verification and weak bus information. |
| 6 | Request the TSP in the affected area turn on capacitor banks and turn off reactors near the weak busses. |
| 7 | OOME fast ramp generators to increase generation in weak bus area. If all the online units in the weak bus area are running at maximum capacity, OOMC units that are available but offline (in weak bus area). |
|  | If |
| 8 | Rerun VSAT with new information. Reference Display: Network Online Sequence |
| 9 | Determine if the Extra-Interface Limit pre-contingency is greater than the Reliability margin value located in the table below. Reference Displays: VSAT Results Page Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. NOTE: If the Extra-Interface Limit pre-contingency value is greater than the Reliability margin value, no further action is required. If not, proceed to Step 12. |
| 10 | If necessary, contact VSAT Support and have them verify the the results from the VSAT application on the weak bus information. |
| 11 | If it was determined that VSAT results were not an actual problem. No further action is required and the system may be restored back to the original state. |
| 12 | Determine if there are more units available in the affected area. If there are more units available in the affected area, repeat steps 6, 7, 8, and 9. |
| NOTE: | If there are no more units available in the area, proceed to step 13. |
| 13 | Ensure that the OPS Support Engineering group has been contacted to devise a mitigation plan. |

# 2.5.3	Issue a Watch

Procedure Purpose: To inform the Market Participants of a Watch.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. - Include the geographical location of the existing overload when notifying Market Participants and TOs. - Before issuing a Transmission Watch, notify the TO, and discuss the actions you are about to take. |
| NOTE: | ERCOT must issue a Watch before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services Or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits established to keep ERCOT within the limits of First Contingency Criteria; - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition; - Conditions have developed such that additional Ancillary Services are needed in the Operating Period; - There is a hurricane in the Gulf with expected landfall in Texas; - A cold front has arrived with temperature anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Market Congestion Management techniques specified in these Protocols will not be adequate to resolve transmission problems; or - Forced Outages or other abnormal operating conditions occur which require operations outside first contingency security limits as defined in the ERCOT Operating Guides; - There are insufficient AS bids. - Adjusted Responsive Reserve below 2500 MW. |
| 2 | Issue a Watch: - Post on the ENS - Post on the MIS - Notify TOs via the Hotline |
| 3 | Using the Hotline, notify all TOs of the Watch. - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.5	 Termination of Notification

Procedure Purpose: To inform the Market of a cancellation of a previous notification.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Advisory, Watch, or Emergency Notice will constitute cancellation of the previous notification. The termination of OCNs does not require a hotline call; however updating the ENS and MIS is necessary. |
| 1 | Update cancellation notice: - On the ENS - On the MIS - Notify TOs via the Hotline |
| 2 | Using the Hotline, notify all TOs when notice has been canceled. - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is canceling the [state Emergency Notice]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.6	 Implement EEA

Procedure Purpose: To implement an Energy Emergency Alert(s) for the appropriate system conditions.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA. EEA in this procedure is to be implemented in concert with the Frequency Control Desk EEA procedures. Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted TOs should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaR as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any level of EEA is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| 1a | Implement EEA 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 1b | Using the Hotline, notify TOs to implement EEA 1. - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA1. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 1 |
| 2a | In addition to measures associated with EEA 1; Implement EEA 2A IF, - EEA 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 2b | Using the hotline, notify TOs to implement EEA 2A. - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2A; - LaaRs are being deployed - If local operating conditions permit, TOs are to reduce customer loads by using distribution voltage reduction measures - Report back to ERCOT when these actions have been initiated and/or completed [ TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2A |
| 2e | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures that have been taken. |
| 3a | In addition to measures associated with EEA 1 & 2A; Implement EEA 2B IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. If no EILS exist, skip EEA 2B and proceed to EEA 3 if needed |
| NOTE: | Unless a media appeal is already in effect, one is required in this level. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation. Notify TOs that a media appeal for voluntary energy conservation is in effect via Hotline. |
| 3b | Using the hotline, notify all TOs to implement EEA 2B. - When TOs have answered the Hotline, print the Hotline log Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2B. EILS are being deployed. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2B |
| 4a | In addition to measures associated with EEA 1, 2A & 2B; Implement EEA 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available |
| NOTE: | Firm load is to be shed in 100 MW blocks. TOs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TSPs shall not manually drop load connected to under-frequency relays during the implementation of EEA. |
| 4b | Using the hotline, notify TOs to implement EEA 3. - When TOs have answered the Hotline, print the Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is implementing EEA 3. ERCOT is instructing all Transmission Operators to shed their share of <amount> MW. Transmission Operators are to report to ERCOT when this is complete and give the amount of load shed. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4d | Instruct the Frequency Control Desk Operator to inform the QSEs via the Hotline that firm load is being shed. |
| 4e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 3 |
| 4f | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures have been taken where possible - Load shed instructions have been received and enacted. |

## 2.5.7	 Restore EEA Steps

Procedure Purpose: Backing out and terminating Energy Emergency Alert(s).

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA Restoration. EEA in this procedure is to be implemented in concert with the Frequency Control Desk EEA procedures. |
| 4a | Restore firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MW |
| 4b | Using the hotline, notify TOs of firm load restoration. - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is instructing all Transmission Operators to restore their share of <amount> MW leaving <amount> MW still off. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load restored. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4d | Ensure the following is posted on the ENS and MIS: - “ERCOT is restoring firm load” |
| 4e | Maintain Adjusted Responsive Reserve supplied from generation equal to 1150 MW while restoring firm load. |
| 4f | Ensure that the Frequency Control Desk Operator notifies the QSEs that firm load is being restored. |
| 4g | Move from EEA 3 to EEA 2B when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MW, AND - All firm load has been restored |
| 4h | Using the hotline, notify TOs of the reduction from EEA 3 to EEA2 B - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B, LaaRs are going to be recalled. Go back to normal, if distribution voltage reductions were made. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings |
| 4i | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4j | Ensure the following is posted on the ENS and MIS: - EEA 3 to EEA 2B |
| 3a | Move from EEA 2B to EEA 2A when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MW, AND - All LaaRs have been recalled, AND - Sufficient Regulation Services exists to control to 60 Hz. |
| 3b | Using the hotline, notify TOs of the reduction from EEA 2B to EEA 2A: - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - EEA 2B to EEA 2A |
| 3e | Appeal through the public news media for voluntary energy conservation may be terminated, notify Shift Supervisors |
| 2a | Move from EEA 2A to EEA 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW, AND - All LaaRs have been restored, or replaced with generation. |
| 2b | Using the hotline, notify all TOs of the reduction from EEA EEA 2A to EEA 1: - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1, all EILS are being recalled, [if Block Load Transfers have been executed please coordinate with ERCOT to restore them as system conditions permit.] [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - EEA 2A to EEA 1 |
| 1a | Move from EEA 1 to EEA 0 when: - EILS resources have been recalled. AND - All uncommitted units secured in EEA 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 1b | Using the Hotline, notify TOs of the reduction from EEA 1 to termination: - When TOs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is terminating EEA. A Watch still remains in effect. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - EEA termination |

# 2.6	Perform Miscellaneous Tasks

## 2.6.1	 Issue Verbal Dispatch Instructions (VDI)

Procedure Purpose: ISSUE a VDI to TO(s) to give a directive.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | VDIs should not re-iterate an instruction given via XML. |
| NOTE: | Whenever a VDI is issued, request the TO to repeat back the instructions. IF the TO Hotline is used to issue a VDI, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the instructions and direct a repeat back again. Continue until an acceptable repeat back is received. |
| 1 | As time permits, complete the VDI form (Desk Top Guide Section 7.4). The following are required fields on all VDIs: - VDI # - EXAMPLE: For the 4th VDI issued by the Transmission and Security Control Desk on May 01, 2009 the number would appear as “T-050109-4” - Operating Day - ERCOT System Operator - Receiving Entity - Receiving Entity’s Operator - Time & Date - Instruction - Reason for Instructions - Intervals - Repeated Instruction back - ERCOT Operator’s signature Blank fields are to have N/A entered. |
| 3 | LOG in the Operator’s Log the VDI information and information relevant to the decision for issuing the VDI. |
| 4 | Forward the VDI form to the Shift Supervisor, as time permits. |

## 2.6.4	 Instructions for Placing a LaaR Hotline Call

Procedure Purpose: Process to inform TOs when LaaRs have been deployed.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | When deploying LaaRs, use the Hotline Call to notify the TOs: - When TOs have answered the Hotline, print Hotline call. Typical script: This is ERCOT operator [first and last name’. ERCOT has deployed LaaRs due to [reason]. That is all, thank you.” |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.6	 Monthly Testing of Satellite Phone System

Procedure Purpose: On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers to ensure ERCOT maintains communication capability via the Satellite Phone System. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in the Operating Procedure Manual for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Attachment B of the ERCOT Satellite Phone User Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form (See Desk Top Guide Section 7.7.3). An electronic copy of this form is located in P:\ SYSTEM OPERATIONS”\Satellite Bridge Testing forms” folder. |
| 4 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is complete. |
| 5 | Log the test date and results in the ERCOT Operations Log. |
| NOTE: | Verify with the Shift Supervisor that the following personnel are notified for any Satellite phone problems during the test by e-mail: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |