Power Operations Bulletin #413
ERCOT has revised the Operating Period Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
2.1.2
Respond to Hour-Ahead Study Results
Procedure Purpose:  To determine A/S scheduling shortage in Hour-Ahead
	Protocol Ref.


	
	
	
	

	
	
	
	
	

	Guide Ref.


	
	
	
	

	
	
	
	
	

	NERC Std.
	
	
	
	


	Approved by:
	Effective Date: May 20, 2009

	Version:
	3.0
	Revision:
	1


	Step
	Action

	1
	REVIEW HA details of the study.

	
	

	2
	VERIFY URS margin is acceptable (not indicated in red or due to rounding errors) and proceed.  

IF in red:
· Select interval with largest deficiency, right click and select “show output for this interval”
(
Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved.

· If deficiency still exists, operators may contact the QSE to request an updated Resource plan.

	3
	VERIFY DRS margin is acceptable (not indicated in red or due to rounding errors) and proceed.  

IF in red:

· Select interval with largest deficiency, right click and select “show output for this interval”

· Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved.

· If deficiency still exists, operators may contact the QSE to request an updated Resource plan.

	
	


	4
	VERIFY RRS margin is acceptable (not indicated in red or due to rounding errors) and proceed.  

IF in red:
· Select interval with largest deficiency, right click and select “show output for this interval”
(
Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved

· If deficiency still exists, operators may contact the QSE to request an updated Resource Plan.

	5
	· Identifying NSRS margin is not possible using the MOI with the implementation of PRR776.
· For NSRS calculations, Resources must also be available, off line and have NSRS checked in the resource plan to be counted in the Excel MAI.
· 





	NOTE:
	If the QSE agrees to correct the deficiency, log and take no further immediate action.  
If they are unable to correct the deficiency (i.e. Insufficient resources are available to provide agreed upon services), then notify the Shift Supervisor of possible protocol violation(s).

	NOTE:
	Once the maximum procurement level has been reached, increasing the offset will not lead to additional balancing deployment.  The maximum procurement level is reached once “Net Gen” and “Net Load” no longer matches in the Real-Time Balancing Market window.

Should Balancing Energy become depleted, over compensating with excessive offsets can potentially cause unexpected deployments when more balancing becomes available.

	NOTE:
	Deployment of NSRS is based on the Excel MAI along with a reasonable load forecast.  Recall is based on real-time UBES availability or other reliability conditions.


	6
	Using the Excel MAI, verify UBES Remaining.

· If >20% of available UBES remains undeployed, no further action is necessary.

· If <20% of available UBES remains undeployed, verify that UBES is available in real-time before entering the offset.
· If >5% of available UBES remains undeployed, no further action is necessary.

· If <5% remaining proceed.

	7

	DETERMINE if NSRS deployment is necessary for balancing support or shortage of physical responsive reserve.  IF NSRS is scheduled and available, deploy for a minimum of one hour and continue as needed.

If NSRS is necessary and is scheduled and available, communicate with the Shift Supervisor to ensure an active constraint won’t be negatively impacted, then deploy NSRS as scheduled and needed to resolve UBES deficiency.

	8


	When NSRS is deployed, ERCOT will provide notice via the ENS with the following information: 
Typical Posting:

“NSRS was deployed in [all zones or specify zone] starting with IE [interval]” 
The termination time of the ENS message must be set to the end of the day, i.e. 23:59.

	9
	Allow NSRS to expire when the percent UBES remaining exceeds the amount of NSRS deployed by 10% or greater.

	10
	When NSRS is terminated, EROCT will provide notice via the ENS with the following information:

Typical Posting:

“At IE [interval], NSRS in [all zones or specify zone] ended. 
The termination time of the message must be set to the end of the day, i.e. 23:59.


2.4
Emergency Operations

2.4.1
Deploying Non-Spin Reserve Service for Diminishing Responsive Reserve

Procedure Purpose: The need to deploy Non-Spin Reserve Service for diminishing Responsive Reserves.
	Protocol Ref.


	
	
	
	

	
	
	
	
	

	Guide Ref.


	
	
	
	

	
	
	
	
	

	NERC Std.
	
	
	
	


	Approved by:
	Effective Date: May 20, 2009

	Version:
	3.0
	Revision:
	1


	Step
	Action

	1
	IF Adjusted Responsive Reserve is less than 2500 MW, check with the Frequency Control Desk to see if a Watch was issued.

	2
	Utilize Non-Spin Reserve Services that can be deployed to increase Responsive reserves.

	Note:
	:Notification is automatically made to the Market Participants at the following link:
http://mospublic.ercot.com/ercot/jsp/balancing_services_mcp.jsp





2.4.2
Non-Spin Reserve Service for Diminishing Responsive Reserve Termination

Procedure Purpose: To provide a guideline to terminate Non-Spin Reserve Service for diminishing Responsive Reserves.
	Protocol Ref.


	
	
	
	

	
	
	
	
	

	Guide Ref.


	
	
	
	

	
	
	
	
	

	NERC Std.
	
	
	
	


	Approved by:
	Effective Date: May 20, 2009

	Version:
	3.0
	Revision:
	1


	Step
	Action

	1
	IF Adjusted Responsive Reserve is greater than 2500 MW, check with the Frequency Control Desk and see if the Watch has been cancelled.

	2
	As system conditions permit, stop the Non-Spin Reserve deployments.

	Note:
	:Notification is automatically made to the Market Participants at the following link:

http://mospublic.ercot.com/ercot/jsp/balancing_services_mcp.jsp












