# Power Operations Bulletin #415

ERCOT has revised the Frequency Control Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.1 	Monitor Generation

# 2.1.1 Capacity and Reserve Monitoring

Procedure Purpose: To determine if there is enough generation to cover the load forecast.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Monitor the current ERCOT System Load and Short Term Load Forecast. Reference Displays: Generation Area Status Short-Term Load Forecast Excel MAI (Market Analysis Interface) |
| 2 | Determine that the current ERCOT System generation capacity is sufficient to meet the Short-Term Load Forecast requirements. Reference Displays: Generation Area Status Excel MAI (Market Analysis Interface) |
| 2a | Compare the current generation and load with the planned capacity values from resource plan at least every other hour. Reference Displays: Generation Area Status Daily Operation Plan – Resource Plan Excel MAI (Market Analysis Interface) |
| 2b | If real-time generation is approaching planned capacity a possible reserve capacity shortage is developing. Discuss situation with Operating Period Desk and Shift Supervisor, and increase monitoring of reserves. Reference Displays: Generation Reserve Status – Available Details Real Time Balancing Market – Balance Bid Tab Real Time Balancing Market – QSE Tab Excel MAI (Market Analysis Interface) |
| 3 | If a projected reserve capacity shortage is developing in the next hour, consider OOMC or deploying of Non-Spinning Reserve Service. Consult with the Operating Period Desk regarding hour-ahead study results. |
| 4 | If OOMC is decided upon, request the Transmission & Security Desk perform the actual instruction. If NSRS is decided upon, request the Operating Period Desk perform the actual instruction. |
| 5 | MONITOR additional available generation capacity and available DC tie capacity. Evaluate amount of additional capacity available in a short time frame using telephone communications to QSEs as appropriate. Reference Displays: Generation Area Status Generation Reserve Status Generation Tie-Line Status |
| 6 | Monitor Responsive Reserves on the QSE Reserve Status Display. If Adjusted Responsive Reserve plus LaaRs is correctly calculated, and is below 2300 MW, - notify the Shift Supervisor - implement EEA - log in the Operator’s Log any decision to declare an EEA |
| 7 | Monitor Ancillary Service Obligations If a QSE is not meeting its Ancillary Services obligations as shown on the QSE Reserve Status Display, - contact the QSE to correct the deficiency - notify the Shift Supervisor of the QSE’s response log the activities performed in connection with this step |

# 2.1.4	VDI for Hold Last Interval

Procedure Purpose: To issue a Verbal Dispatch Instruction to hold the last good interval.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | A Watch must be issued if two (2) consecutive Real-Time Balancing Intervals are held as per procedure 2.6.3 step 1. |
| 1 | If market control mechanisms have failed, or ERCOT has issued erroneous instructions THEN, using the hotline, issue an instruction: - When QSEs have answered the Hotline, print Hotline Log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#]. Hold the [interval ending time] Balancing Energy deployments until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | To resume with Real-Time Balancing deployments, using the hotline, issue an instruction: - When QSEs have answered the Hotline, print Hotline Log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time]. Resume with the [interval ending time] Balancing Energy deployments. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | As time permits complete the VDI form (See Desk Top Guide Section 7.4), using these instructions: - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows – write in “Hold interval ending <time>, resume with interval <time> - Instruction repeated back ALL fields are to have either pertinent data or N/A entered. Leave NO field(s) blank. |
| 4 | A held interval message must be posted on the MIS and ENS: Typical posting: Real-time balancing deployments were held for IE XX:XX. |
| 5 | LOG in the Operator’s Log the VDI information and reason(s) why interval was held. |
| 6 | Ensure printed Hotline log has date, time, and reason for call information. Forward, along with VDI to the Shift Supervisor, as time permits. |

# 2.2.2 	Site Failover Hotline Message

Procedure Purpose: To inform the QSEs when a planed site failover is about to occur.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Using the hotline if available notify all QSEs before the scheduled time for a planned site failover (preferably five (5) to 30 minutes). The following message should be communicated. The variable information is in brackets. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [time], ERCOT will perform a planned site failover of its Energy & Market Management Systems from [Taylor] to [Austin]. During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about five minutes. All systems should reestablish communications automatically.” |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5	Frequency Control

# 2.5.1	Frequency Control Operating Procedure

Procedure Purpose: To maintain system frequency within acceptable levels.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| 1 | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or - “Last AGC Cycle” time on Generation Area Status display is not updating or AGC operation adversely impacts the reliability of the Interconnection If the problem can’t be resolved quickly, place a large QSE (that has regulation reserve) on constant frequency. |
| NOTE: | - In the scenario where AGC operation adversely impacts the reliability of the interconnection, (ERCOT is handing over the frequency control to a large QSE), ERCOT AGC should be placed into the MONITOR mode. |
| 2 | Using the Hotline, notify all QSEs that ERCOT is having computer issues and is putting a QSE on constant frequency. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is currently having computer issues and has put a QSE on constant frequency until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 3 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| NOTE: | If the QSE that is put on constant frequency is having trouble keeping up, issue fleet VDI’s to other QSE’s to help out or put a different QSE on constant frequency. Remember to take the first QSE off constant frequency. For low frequency refer to 2.5.2, Operator Instructions for Low Frequency. For high frequency refer to 2.5.5, Operator Instructions for High Frequency. |
| 5 | When frequency control is functioning, remove the QSE from constant frequency. |
| 6 | Notify all QSE’s by Hotline that ERCOT is back on control. - When QSEs have answered the Hotline, print Hotline log. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is back to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| 7 | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| 8 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 9 | At the operator’s discretion, turn off SCE feedback for Regulation Providers with Participation Factors less than 1% (<0.01). |
| 10 | Monitor QSE generation and SCE: - Remove a QSE’s SCE feedback if they have a large SCE and their generation is not moving in the proper direction or rate to correct their SCE. Reference Display Responsive, Regulation, and SCE Regulation |
| 11 | NEVER (unless directed by the Control Engineer or designee): Modify “Total (SCE-responsive) Feedback Gain” (should be altered by the Control Engineer) - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) Reference Displays: Responsive, Regulation, and SCE – Details |
| 12 | LOG in the Operator’s Log frequency deviations of greater than or equal to 0.10 Hz. Record the following: - Possible reasons if known. (SCE, Large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped. - Approximate MW that was on the unit when the unit tripped. - Approximate ERCOT load. |

# 2.5.3	Actions When Frequency Telemetry is Incorrect

Procedure Purpose: To prevent the unnecessary deployment of Responsive Reserve due to incorrect telemetry frequency data.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | IF frequency is BELIEVED to be incorrect VERIFY that the frequency is correct by comparing the data from multiple sources. - Go to the “Generation Area Status” display, and click on the “i” to the left of “Current Frequency” to view “OPA Measurement” window. |
| 2 | In “OPA Measurement” window, under “Status” column, check “Prime” on a valid frequency source. |
| 3 | LOG in the Operator’s Log any relevant information on this event. |
| NOTE: | - The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may view the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency |
| 4 | If frequency is below 59.91 Hz and continues to decay, implement the following action as necessary: - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available to recover frequency. - When issuing the VDI, the operator should request enough generation to restore frequency. |
| 5 | When Regulation Service is available, back in service and the frequency is normal, release the Fleet VDI. |

# 2.5.4	Monitor and Control Time Error Correction Schedules

Procedure Purpose: This procedure will establish the standard for implementing time error correction

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT ISO is the Reliability Coordinator and Balancing Authority that implements and terminates ERCOT Time Corrections in accordance with ERCOT Protocols and Operating Guides. ERCOT Reliability Coordinator is the Interconnection Time Monitor within the ERCOT Interconnection. |
| REQUIREMENTS: | When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. Time error corrections normally start and end on the hour or half-hour. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction. However, at no time should the accumulated time error be allowed to exceed five (5) seconds. Time error correction notifications shall be labeled alphabetically on a monthly basis (A-Z). In the succeeding month, the first time error correction will revert back to “A”. |
| 1 | DISPLAY the Generation Area Status display. Reference Display: Generation Area Status – Time Error – “Correction Schedule” |
| 2 | Select Time Error – Correction Schedule. |
| 3 | ENTER the appropriate Time error ID letter. |
| 4 | ENTER the frequency offset using – 0.02 for fast time correction (59.98 Hz) or +0.02 for slow time correction (60.02 Hz). |
| 5 | ENTER a Start Time later than the current time AND ENTER a Stop Time later than the scheduled start time. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 6 | Notify all QSEs using a hotline call, if available, before starting time correction, of the start time and frequency offset. Typical script: “This is ERCOT operator [first and last name]. ERCOT is initiating a time error correction, we will ENTER the frequency offset using [– 0.02] or [+0.02] at [time]. The current time error is [time]. Thank you.” Print Hotline Log, ensure printout has date and time, and forward to Shift Supervisor. |
| 7 | VERIFY the Manual radio button to be selected. Time correction will start at selected date and time. Reference Display: Generation Area Status – “Time Error” – Correction Schedule |
| 8 | Monitor the time error on the Generation Area Status Display until it reaches an acceptable value (+/- 0.5 seconds). Time error correction may be terminated after five hours, or after any hour it has reached an acceptable value of +/- 0.5 seconds. |
| 9 | If a time error correction is prematurely terminated, wait at least one hour between sending the termination and re-initiation notices. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 10 | - Notify all QSEs using a hotline call, if available, before ending time correction. Typical script: “This is ERCOT operator [first and last name]. ERCOT is ending the time error correction at [time]. The current time error is [time]. Thank you.” - Print Hotline Log, ensure printout has date and time, and forward to Shift Supervisor. |
| 11 | LOG in the Operator’s Log start time, stop time, Time error ID letter, time error, and frequency offset for each start and termination. |

## 2.6.1	 Issue an Operating Condition Notice (OCN)

Procedure Purpose: To inform the QSEs of a system Operating Condition Notice.

| Protocol Ref. | 5.6.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.1 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Operating Condition Notice (OCN) IF: - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the National Hurricane Center (http://www.nhc.noaa.gov) - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - There is a projected reserve capacity shortage and/or projected balancing energy bid shortage. |
| 2 | Issuance of an OCN requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of OCN. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an OCN for [state OCN]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.2	 Issue an Advisory

Procedure Purpose: To inform the QSEs of a system Advisory.

| Protocol Ref. | 5.6.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.2 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Advisory IF: - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the “National Hurricane Center” http://www.nhc.noaa.gov - When ERCOT recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability - When weather or ERCOT System conditions require more lead-time than the normal Day Ahead market allows - Transmission system conditions indicate ERCOT is likely to exceed established limits and no practicable resource solution exists - Loss of communications or control condition is anticipated or significantly limited - If ERCOT is unable to comply with any of the market timing deadlines in the Day Ahead or Adjustment Period, or omits one or more procedures in the scheduling process) - Adjusted Responsive Reserve drops below 3000 MW - When long-range notice (approximately 48 hours) is needed to ensure the secure operation of the ERCOT system, alert the Market Participants to a potential threat to reliable operations with the following: - Lead time for dual fuel generating units to prepare for fuel supply problems in the event of anticipated severe cold weather - Any other operational concerns |
| 2 | Issuance of an Advisory requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of Advisory. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory for [state Advisory]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.3	 Issue a Watch

Procedure Purpose: To inform the Market Participants of a system Watch

| Protocol Ref. | 5.6.5 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.3 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must issue a Watch before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services, or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits with no practicable resource solution - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - There is a hurricane in the Gulf with expected landfall in Texas - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A situation is emerging that will have an adverse effect on grid reliability - Loss of communications or control condition is pending or in progress. - Adjusted Responsive Reserve drops below 2500 MW - ERCOT holds two (2) consecutive Real-Time Balancing intervals |
| 2 | Issuance of a Watch requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Watch. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.4	 Issue an Emergency Notice

Procedure Purpose: To inform the Market Participants of an Emergency Notice.

| Protocol Ref. | 5.6.6 | 4.8 |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.4 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notifications. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no practicable resource solution exists. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures. |
| 2 | Issuance of an Emergency Notice requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Emergency Notice. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.5	 Termination of notification

Procedure Purpose: To inform the QSEs of a cancellation of a previous notification.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | If a condition increases in severity, then the posting of the corresponding Advisory, Watch, or Emergency Notice will constitute cancellation of the previous notification. The termination of OCNs does not require a hotline call; however updating the ENS and MIS is necessary. |
| 1 | Update cancellation notice: - On the ENS - On the MIS - Notify QSEs via the Hotline |
| 2 | Using the Hotline, notify all QSEs when notice has been canceled. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is canceling the [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits |

## 2.6.6	Implement EEA

Procedure Purpose: To implement an Energy Emergency Alert(s) for the appropriate system conditions.

| Protocol Ref. | 5.6.7 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.5.3.2 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Frequency Control Desk will implement applicable levels of the EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaR as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any level of EEA is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3 |
| 1a | Implement EEA 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 1b | Using the hotline, notify QSEs to implement EEA 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 1, QSEs are to do the following: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 1 |
| 1e | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources |
| 2a | In addition to measures associated with EEA 1 Implement EEA 2A IF: - EEA 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 2b | Using the hotline, notify QSEs to implement EEA 2A. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2A; ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to QSEs to deploy all LaaRs bid to supply Responsive Reserves Service within ten (10) minutes. Also: - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that LaaR have been deployed. |
| 2d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2A |
| 2f | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources. - LaaRs have been deployed. |
| NOTE: | Unless a media appeal is already in effect, one is required in this level. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation |
| 3a | In addition to measures associated with EEA 1 & 2A; imPLEMENT eEA 2B IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. If no EILS exist, skip EEA 2B and proceed to EEA 3 if needed. |
| 3b | Using the hotline, notify QSEs to implement EEA 2B. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2B. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources in the current time period until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that EILS Resources have been deployed. |
| NOTE: | EILS Resources have 10 minutes to comply with this instruction. If conditions develop that require implementing EEA 3, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| 3d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2B |
| 4a | In addition to measures associated with EEA 1, 2A, & 2B; Implement EEA 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| 4b | Using the hotline, notify QSEs to implement EEA 3. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 3. Transmission Operators have been instructed to shed <MW Amount> of firm load. QSEs confirm that their generation resources are at maximum output. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 4d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 3 |
| 4e | VERIFY the following: - All Generation Resources are at full capacity - Available Non-Spin has been deployed - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended - All LaaRs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

## 2.6.7	Restore EEA

Procedure Purpose: Backing out and terminating Energy Emergency Alert(s).

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA Restoration. Numbering of procedure steps is reversed to coincide with EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. |
| 4a | Restore firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MW |
| 4b | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. Using the hotline, notify QSEs of the restoration of firm load: - When QSEs have answered the Hotline, print the Hotline log Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is currently restoring firm load. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Move from EEA 3 to EEA 2B when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored. |
| 4d | Using the hotline, notify QSEs of the reduction from EEA 3 to 2B, if 2B was skipped move from EEA 3 to 2A : - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B.” QSEs that deployed LaaR in EEA 2A may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4e | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4f | Ensure the following is posted on the ENS and MIS: - EEA 3 to EEA 2B |
| 4g | Instruct the Transmission & Security Desk Operator to notify the TOs that LaaRs are being restored. |
| NOTE: | Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LaaRs are being restored |
| 3a | Move from EEA 2B to EEA 2A when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 3b | Using the hotline, notify all QSEs of the reduction from EEA 2B to EEA 2A: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - EEA 2B to EEA 2A |
| 3e | Instruct the Transmission & Security Desk Operator to notify the TOs that ERCOT moved from EEA 2B to EEA 2A. |
| 3f | Appeals through the public news media for voluntary energy conservation may be terminated, notify Shift Supervisor |
| 2a | Move from EEA 2A to EEA 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW AND - All LaaR have been requested to be restored or replaced with generation |
| 2b | Using the hotline, notify QSEs of the reduction from EEA 2A to EEA 1: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1. QSE’s that deployed EILS Resources in EEA 2B may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - EEA 2A to EEA 1 |
| 2e | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS Resources are being recalled. |
| 1a | Move from EEA 1 to EEA 0 when: - EILS Resources have been requested to be recalled AND - All uncommitted units secured in EEA 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 1b | Using the hotline, notify QSEs of the reduction from EEA 1 to EEA 0: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is terminating EEA. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - EEA termination |
| 1e | Instruct the Transmission & Security Desk Operator to notify the TOs of the termination of EEA. |

## 2.6.8	 Provide Advanced Notice of Diminishing Responsive Reserve

Procedure Purpose: Guidelines for issuing advance notice of diminishing Responsive Reserves

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory has been issued. |
| 4 | Ensure the following is posted on the ENS and MIS: - Advisory issued for ARR below 3000 MW. |
| 5 | When adjusted Responsive Reserve falls below 2500 MW: Using the Hotline, notify QSEs: - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. - Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. - Suspend all ERCOT required generation unit testing. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure Non-Spin has been deployed. |
| 7 | OOME to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0. Follow up with a Settlements only VDI stating :OOMC for Quick-start” on the VDI form. |
| 8 | Instruct the Transmission & Security Desk Operator to notify the TOs that a Watch has been issued. |
| 9 | Ensure the following is posted on the ENS and MIS: - Watch issued for ARR below 2500 MW. |

## 2.6.9	 Diminishing Reserve Notice Cancellation Guidelines

Procedure Purpose: To provide notifications and back out of the actions taken during diminishing system reserves.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
| 1 | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
| 2 | As system conditions permit, recall/release incrementally, any additional generation that was brought online to recover ARR. |
| 3 | Cancel a Watch or Advisory when: - All related OOM and Non-spin deployments have ended, AND - ARR is >= 3200 MW, AND - Load is trending down, OR - The Excel MAI shows the “Max Cap Room” increasing over the next two hours |
| 4 | . IF a watch has been canceled, - NOTIFY QSEs that testing may be resumed. Typical scripts: Cancel Advisory - “This is ERCOT operator [first and last name]. ERCOT is canceling the Advisory for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 3000 MW. [QSE] please repeat this back to me. That is correct, thank you.” Cancel Watch - “This is ERCOT operator [first and last name]. ERCOT is canceling the Watch for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 2500. MW. At this time, performance testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 6 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory or Watch has been cancelled. |

## 2.6.10	 Potential DCS Event – Use of LaaRs to Arrest a Low Frequency Disturbance

Procedure Purpose: To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | There are times when the MW amount lost will be more than the NERC reportable amount. In these cases LaaRs will still need to be used to recover frequency |
| NOTE: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than scheduled frequency prior the disturbance. Within 90 minutes ERCOT shall fully restore its Contingency Reserves to the pre-contingency level. This 90 minute restoration period begins at the end of the disturbance recovery period. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1083 MW OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1083 MW. It is anticipated that the deployment of LaaRs will occur in stages. LaaRs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, a text message may be sent as time permits so as not to impede system operations. In order to control frequency, be prepared to issue a “Fleet Down” VDI once the system has recovered to its scheduled/pre-disturbance frequency value. |
| 1 | When a low frequency disturbance occurs due to a loss of generation, DETERMINE immediately, by calculating the loss of generation, if the event is potentially a NERC Reportable DCS Event. |
| 2 | If a low frequency disturbance occurs, AND there is NO indication of a generation loss, determine the magnitude of the event by using the “Filtered ACE Incremental MW Requested” tag, assume that a potential DCS event has occurred and SCADA communications has been lost if the total generation loss is greater than 1000 MW, , implement Step 4. - Determine the magnitude of the event by using the “Filtered ACE Incremental MW Requested” tag on the “ERCOT & QSE Summary Page” in PI. - Take care to calculate the entire generation loss from the PI tag, not just the difference between zero and the lowest number. Example: If the “Filtered ACE Incremental MW Requested” pre-disturbance value is +150 MW, and post disturbance value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. |
| 3 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 4 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - When system conditions warrant, issue a VDI using the hotline instructing QSEs to deploy ALL un-deployed LaaRs and hydro generation that are bid to supply Responsive Reserve. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs and instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Verbal Dispatch Instruction instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct; I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Ensure printed Hotline Log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 6 | Complete the VDI form (See Desk Top Guide Section 7.4) and process. - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows: “All QSEs are required to deploy any un-deployed LaaRs and hydro supplying Responsive Reserve due to a potential DCS event.” |
| 7 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being deployed. |
| NOTE: | verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| 8 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being restored. |

## 2.6.11	 Response to Frequency Decay

Procedure Purpose: Response to severe frequency decay, up to and including, using EEA 2A and the deployment of LaaR.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | UFRs will deploy as follows: Hydro RRS - 59.90 Hz RRS LaaR – 59.7 Hz |
| 1 | If Regulation Service is depleted, AND frequency is below 59.97 Hz and continues to decay, implement the following actions as necessary: - Ensure any remaining Balancing Energy is deployed. - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available. - When issuing the VDI, the operator should request enough generation to restore frequency and recall approximately 50% of Regulation Up Service. |
| 2 | VERIFY that the Balancing Offset is set to an approximate value that will restore Regulation Service. |
| 3 | IF frequency continues to decay, ENSURE 33% of the TOTAL Responsive Reserve Service is deployed (approximately 760 MW). |
| NOTE: | On depletion of the first 33% of TOTAL Responsive Reserve, ERCOT shall declare an EEA in effect (Protocols Section 6.7.3). |
| 4 | IF Step 3 of this procedure does not arrest the frequency decay AND frequency reaches 59.85, IMPLEMENT EEA 2A and deploy ALL LaaR bid to supply Responsive Reserve. |
| 5 | Follow EEA Procedures as required per section 2.6.6. |
| NOTE: | Verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| NOTE: | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency Refer to procedure 2.5.3 for Actions When Frequency Telemetry is Incorrect. |

## 2.6.12	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the Back-up Control Center (BCC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC, THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the BCC - Notify them of the situation AND - Have them attempt to make contact with Security at TCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT is declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Issue a VDI to the QSE that was put on constant frequency, as time permits. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support, Telecommunications - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Most potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission/inder Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.6.13	Restoration of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Frequency Control Desk Operators at the Back-up Control Center (BCC) in restoring Real-Time operations.

- Additional staff has arrived, including a Shift Supervisor,

- BCC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | As additional Operators arrive, be sure to communicate any pertinent information that will assist them in getting their specific functions ready for normal operation. |
| Restoring Frequency Control | When an Operating Period Desk Operator has arrived, had time to get the offset calculation spreadsheet caught up, and is able to enter offset values into the MOI: IF: - Holding Real-time Balancing Energy Market (RTB) deployments, THEN: - Verify the proper operation of the RTB and that deployments are being sent to the Market Participants (MP) AND - Remove the QSE that is put on constant frequency. |
| Market Notification | IF: - RTBM is running and valid deployments are being sent, THEN: - Place the following QSE Hotline call: * * * WARNING * * * When removing a QSE from constant frequency control, remove ERCOT AGC from Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT is resuming normal, Real-Time operations from the back-up control center. Please continue to direct all phone calls to (512) 225-7100. ERCOT is ending VDI [#] at [time]. Resume with the [interval ending time] Balancing Energy deployments. [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Additional Notifications | Notify the following: - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations and/or designee - Engineering Support - These phone numbers have been programmed into the control room cell phone. |
| Notification of Additional Operators | WHEN: - All functionality has been resumed at the BCC, THEN: - Notify the additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System. |
| Contact Security | Notify Security that the transition of Operations to the BCC has been completed |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |

## 2.7.12	Emergency Energy across the SPP DC Ties for EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the SPP DC tie(s) in an Energy Emergency Alert 2A, 2B or 3.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE: | If ERCOT goes directly to an EEA 2A, 2B or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below. |
| 1 | Notify the SPP Reliability Coordinator or ERCOT’s EEA status Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will contact the Tariff desk to inquire about the availability of emergency transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the emergency transmission service available. Thank you.” |
| NOTE: | ERCOT must have the Reliability Coordinator Information System (RCIS) updated with the EEA 2 or 3 status before SPP grants emergency transmission service. |
| NOTE: | SPP will curtail all non-firm transmission service schedules going out of ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-Tag(s). Proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status: Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| NOTE: | Keep SPP informed of ERCOT’s status. |

## 2.7.14	Fast Start Emergency Energy to SPP

Procedure Purpose: Steps to provide emergency assistance to Southwest Power Pool across the SPP DC ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 0520/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Every effort should be made to render assistance during emergency conditions. SPP will notify ERCOT that emergency assistance is needed. |
| 1 | VERIFY that providing emergency assistance to SPP will not put ERCOT in an insecure state, or worsen an existing insecure state. |
| NOTE: | SPP will contact the DC Tie Operator and arrange to maximize the DC tie output into SPP. It is not necessary to confirm that an emergency condition has been posted in the Reliability Coordinator Information System (RCIS). SPP may need to act before the RCIS is updated. |
| 2 | Notify the Operating Period Desk to adjust the Offset to minimize the use of Regulation. |
| 3 | When possible: - Contact AEP QSE and instruct them to create and submit an E-Tag for the emergency assistance (this can be done after-the-fact but within an hour of the event). - Issue a VDI to AEP QSE for the emergency assistance. |