Power Operations Bulletin # 416

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.1.3	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | If RTCA or the State Estimator has not solved within the last 15 minutes, refer to Desk Top Guide Section 3.1 and run through the checklist. If, after trying all the checks and RTCA and/or the State Estimator still has not solved, notify the on-call State Estimator Support Engineer and request the tool(s) be restored to operation as soon as possible. If RTCA will not solve but the EMS is available notify the on-call Operations Engineer to request limits be calculated manually. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 30 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to the ERCOT Transmission Operators: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 30 minutes. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of their respective limits. Continue to monitor voltages in your area. Notify ERCOT of any abnormal line operations in your area.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Once RTCA and State Estimator are operational: Make a Hotline call to the ERCOT Transmission Operators: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator are now functioning and we are now back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 4 | If VSAT has not solved within 1.5 hours: - Manually run VSAT - If no results, contact Operations Planning Support - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. - If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |

# 2.1.4	OOME – VDI Guidelines

Procedure Purpose: To provide guidelines for OOMEs and VDIs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 1 does not apply to wind units. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOME’d off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, coordinate with the Frequency Operator for issuance of VDI to relieve the QSE from their Ancillary obligation if necessary. - Issue an instruction to release the QSE from the dispatch instruction so they can come back into compliance. |
| 5 | When an SPS activates and that SPS activation de-rates a resource or takes a resource off line, issue a VDI to the affected QSE. - The beginning time on the VDI will be the interval that the SPS activated. - The ending time on the VDI will be the interval the SPS was restored to service. - The exception will be VDI’s will not exceed four (4) hours after the time of activation. - If the resource is a DC tie, include the name and zone of the tie. Typical Script on the VDI: “SPS activation, caused <unit name or DC tie name> to <trip or runback>”. |
| 6 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with a Settlements only VDI stating “OOMC for Quick-start” on the VDI form. |
| 7 | As time permits, forward the VDI to the Shift Supervisor |

# 2.1.6	Monitoring Priority Outages in Real Time Monitor Mode

Procedure Purpose: To monitor priority outages in real time.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | A priority outage is one that affects generation. |
| 1 | Select the required outage or outages in the Outage Scheduler to be monitored in the Real-Time Monitor. |
| 2 | Select the “Toggle Monitor Flag” from the drop down and Apply. |
| 3 | Select switch to the Real-Time Monitor to view the monitored outage or outages. |
| 4 | Verify that the outage is being monitored by change in color to pink. |
| 5 | Monitor outages as required. |
| 6 | When a priority outage returns to service ensure the generation that was being dispatched is released when appropriate. |
| 7 | Notify the Shift Supervisor and make log entry as time permits. |

# 2.2 	Manage Transmission Congestion

# 2.2.1	Real Time Contingency Analysis (RTCA)

Procedure Purpose: To have situation awareness of the transmission system

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit violations. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. |
| NOTE: | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Energy Management System (EMS) and an electronic copy is located on the ERCOT website under ‘Grid Information’ in the Transmission section. http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA) in the key document section. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 20 minutes. |
| 3 | If RTCA has not run within 20 minutes, refer to Section 2.1.3, Analysis Tool Outages. |
| 4 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist: - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are usually located in the daily Outage Notes. |
| 5 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or -4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take appropriate voltage control action. |
| 6 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 7 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Desk Top Guide Section 3.6 for guidance. |
| 8 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 9 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 10 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 11 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Proceed to section 2.2.3 Potential IROL’s. . If the system operator determines that the Pre-contingency value or system topology is incorrect, OR if a SPS, RAP, PCAP, TOAP, or MP exists, step 10 may be omitted. |
| 12 | If congestion management techniques fail to resolve congestion and no practicable resource solution exists, ISSUE a Watch per section 2.5.3. |
| 13 | Periodically check the Base Case violations display for Thermal overloads. A “thermal overload in real-time” means loading above 100 % of the NORM/Continuous rating. |
| 14 | If a valid Thermal overload exists in real-time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 15 | Periodically check the “Contingency Solution Results” display. If there are unsolved contingencies, run the State Estimator again. If unsolved contingencies remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. If there are known reasons that the contingency is unsolved, as time permits, notify the on-call Operations Support Engineer to verify system conditions have not changed.. |

# 2.2.2 	Real Time Constraint Activity Manager (RTCAM)

Procedure Purpose: To alleviate congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Local Congestion Management Techniques consist of OC3s, Unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| NOTE: | Phase shifters could at times be used to help with congesting management: - Putnam – NW/WN transfers to increase CSC transfer capability - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |
| 1 | VERIFY SFT is enabled in the MOI. - This can be determined by making sure that the check box next to “Run SFT for Real-Time Markets” on the Real-Time Balancing Market display is checked. If it is not checked, then check it. |
| 2 | DETERMINE if RTNET and RTCA has solved within 20 minutes. |
| 3 | If RTNET and RTCA have not solved within 20 minutes, refer to Section 2.1.3, Analysis Tool Outages. |
| 4 | DETERMINE if RTNET has solved with a solution status of “VALID SOLUTION – NO SFT CASE.” - If RTNET has this solution, notify the State Estimator On-Call Engineer. |
| 5 | If RTCA has solved within 20 minutes, EXAMINE the RTCAM Branch Violations and Operating Constraints List. |
| 6 | EXAMINE the constraints with the “Active” check box filled in. - VERIFY that an OC3 is created for all overloaded active constraints in the MOI by selecting the “constraint” tab from the “Real-Time Balancing Market” screen in the MOI. In the Type column, sort descending. All OC3s will be sorted to the top of the page. - If an overloaded constraint is active in RTCAM, but the corresponding OC3 is missing from the MOI, LOWER the value in the “% Rating” column in RTCAM to tighten the constraint until the OC3 appears in the MOI. - If an OC3 is active in the MOI, but the corresponding constraint in RTCAM is well below the monitored rating, INCREASE the value in the “% Rating” column in RTCAM to loosen the constraint. |
| 7 | When an OC3 deploys quick start units for congestion, do one of the following: - Issue an “OOMC VDI” for settlements on the quick start unit(s) that are required to mitigate congestion - Issue an OOME for quick start unit(s) using the OOM tool and keep the OC3 active, or - Use OOM tool to OOME for quick start unit(s) instead of activating an OC3, or - Issue a VDI to disregard the unit specific deployment and write “instructed deviation” on the VDI if congestion can be resolved without unit(s) OOMC VDI for quick start units will only be given under the local congestion scenario, balancing and zonal deployments are not included. Follow up with a Settlements only VDI stating “OOMC for Quick-start” on the VDI form. |
| 8 | To activate a constraint, check the “Active” check box next to the constraint to be activated. The text in this row of data will change to red and it will be immediately sorted to the top of the display. |
| 9 | To deactivate a constraint, uncheck the “Active” check box next to the constraint. Uncheck the “Retain” check box as well, if desired. Leaving the “Retain” box checked will only cause the constraint to remain on the Operating Constraints List display when an overload is not occurring. |
| 10 | To acknowledge constraints that are determined to be erroneous or are already accounted for, check the check box in the “Ack.” Column. This will sort the constraint to the bottom of the display. |
| 11 | Special Protection Schemes (SPS), Remedial Action Plans (RAP), and Pre-Contingency Action Plan (PCAP) analysis - EXAMINE the results in RTCAM for RAP or SPS activation, using the “SPS” and “RAP” columns on the Operating Constraints List display. - If “SPS” and/or “RAP” is checked, EXAMINE the color of the background. Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. - ADJUST initial “% Rating” higher if activating a constraint for a post-RAP/SPS overload if needed. This is because RTCAM/SFT can not model RAP/SPS when generating OC3 constraints so they tend to over-constrain at 100 % of rating. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |

# 2.2.3 	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| NOTE: | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, and if a SPS, RAP, PCAP, TOAP, or MP does not exists; this is considered to be a potential IROL. Corrective action must be taken within 30 minutes to reduce the flow below 125%. |
| 1 | If congestion management techniques fail to reduce the flow below 125% and no practicable resource solution exists, take real-time snap shot and save it so analysis can be done at a later time. |
| 2 | Notify the Shift Engineer or the on-call Operations Support Engineer, ask for a Mitigation Plan. |
| 3 | Make log entry. |

# 2.2.4 	OOME when OC3 is not Effective

Procedure Purpose: A process to relieve congestion when an OC3 is not effective.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | All wind units have the non-bid flag checked in the Resource Plan which will prevent them from receiving local congestion instructions. When OC3 activation is not effective due to excessive wind generation output, the following steps shall be taken to OOME wind generation to relieve transmission congestion. |
| 1 | Activate an OC3 for local congestion as mentioned in Section 2.2.1. |
| 2 | Upon activation of the OC3, perform a Contingency Analysis study as indicated in Section 3.1 of the Desk Top Guide. |
| 3 | After performing a Contingency Analysis study, navigate to the Network Constraints Summary by going to Analyst Displays  Contingency Analysis Displays  Shift Factors, or typing NETSENS_CONSTRAINTS in the command line at the top of the display. |
| 4 | On the Network Constraints Summary Display, scroll to the constraint for which the corresponding OC3 was created. Click on the circle with an “i” inside it on the right hand side of the display. This will bring up the Network Constraints Details. |
| 5 | The Network Constraints Details display shows all units which have positive or negative shift factors above 1 % for the given constraint. Scroll through this list to find the wind units with the greatest positive shift factors. Note that this does not apply to the McCamey Area units, see procedure 2.2.10 when OOMing those units. |
| 6 | If local techniques fail to maintain system security, an Emergency Notice must be declared before Zonal Techniques may be utilized. |

# 2.2.5  	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: Processes to relieve local congestion surrounding the CFE DC-Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. |
| NOTE: | ERCOT may adjust generation to solve local congestion in the areas of the CFE DC-Ties; however OOMC’s will not be utilized to allow schedules to flow. |
| NOTE: | When curtailing E-tags for transmission issues, they should only be curtailed for a couple hours at a time, hourly if possible. |
| 1 | Update RTMONI with the CFE DC-Tie Limits each night across midnight. |
| 2 | If E-Tags must be curtailed to control post-contingency overloads: - Contact the ERCOT DC-Tie Operator to have the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 3 | If E-Tags must be curtailed to control the Valley or Laredo Import: - Contact the ERCOT DC-Tie Operator once the Valley or Laredo Import is at 90% and will continue to climb. - Request to have the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 4 | If curtailments are being made, keep RTMONI updated with new limits. |
| 5 | As room becomes available, keep the ERCOT DC-Tie Operator notified so E-tags can be re-loaded |
| 6 | ERCOT must declare a Transmission Watch or Emergency in order to curtail E-Tags immediately. If a Watch or Emergency has been declared for a transmission issue: - Contact ERCOT DC-Tie Operator to have the appropriate DC-Tie ramped to needed MW level - Ensure the Transmission Watch or Emergency has been posted on the ENS and MIS - Notify the Shift Supervisor |
| 7 | ERCOT will curtail E-Tags for CFE for their transmission issues or emergencies. If contacted by AEP Corpus of a CFE issue: - Identify if at least 20 – 30 minute notice can be given for curtailment - Notify ERCOT DC-Tie Operator with information to make curtailment - Notify the Shift Supervisor |

# 2.2.6 	Zonal (CSC) Congestion Management

Procedure Purpose: To relieve zonal congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTES: | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. The CSC Limits are computed and posted on the ERCOT website by Operation Support Engineering during the day-ahead planning process. These limits are based on the day-ahead Resource Plans and forecasted system conditions. Potential IROLs are defined in the day-ahead analyses or when changes in system conditions warrant further evaluation. If a CSC has been marked as an IROL on the “Transmission Limits” sheet, ensure the limit is honored. If the limit is exceeded, take all possible actions to get below the limit in 30 minutes or less. An OC1 should only be utilized for a zonal overload where both the contingency and the overloaded element include a CSC and/or CRE. A current list of CSC/CRE DATA is posted on the following ERCOT website: http://mospublic.ercot.com/ercot/jsp/csc_cre.jsp |
| 1 | Monitor and update the RTMONI limit page at least once an hour. The number should be rounded to a whole number. |
| 2 | When the CSC actual flow approaches or exceeds the limit from the “Real-Time CSC Limit Calculator”, Activate the OC1 |
| 3 | When RTCA shows a post contingency zonal overload and the CSC has not exceeded its’ limit on the “Real-Time CSC Limit Calculator, AND RTCA has solved within the last 10 minutes, then RTCA results should be used as a basis for managing zonal congestion, activate the OC1. When the zonal overload has been resolved, restart the Real-Time CSC Limit Calculator for a new CSC limit. |
| 4 | If RTCA shows a post contingency zonal overload and the Real-Time CSC Limit Calculator has run, the application will display the letters OL (Over Limit). Once the zonal overload has cleared in RTCA, restart the Real-Time CSC Limit Calculator application by activating the manual Run Sequence on RTCA. |
| 5 | If the Real-Time CSC Limit Calculator has run and the application does not display a limit and the element displays “Basecase overload”, “Temporarily Unavailable” or “Min West”; the previously published value will remain the same unless RTCA indicates a thermal or post contingent overload. |
| 6 | In the event the Real-Time CSC Limit Calculator is inoperable. Post the limits from “Transmission Limits to be Monitored” daily report to RTMONI. If RTCA shows a post contingency overload before we get to the posted CSC limit start controlling to RTCA and post limit in RTMONI. If you have reached the CSC limit and it hasn’t come in on RTCA, keep raising the posted limit until the new limit is defined by the RTCA results, then post it in RTMONI and start controlling to the new CSC limit. |
| 7 | The W-N and N-W OC1 should not be used for a contingency overload through the Putnam 138KV line UNLESS the Putnam Phase-Shifter is out of service. If an overload on the Putnam 138kV lines shows in RTCA, have AEP adjust the phase-shifter set point lower to clear the overload. |
| 8 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques: - OOME/VDI resource down - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to help control the [zone – zone] CSC.” |
| NOTE: | If Zonal Management Techniques failed to control Zonal Congestion and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |
| 9 | A PCAP exists to manage North – South congestion by opening the 138kV line between Goldthwaite and Brownwood. The following reliability actions should be taken: - Activate the North – South OC1 - Run a real-time snapshot study to determine if the PCAP works - The PCAP will cause local congestion, determine if enough generation can be moved to resolve the congestion. - If so, activate the OC3 and deactivate the OC1 - If not, keep the OC1 activated |
| 10 | If Local Techniques fail to control a non zonal post contingency overload involving CSC/CRE elements within 30 minutes, utilize Zonal Congestion Management Techniques. - A transmission condition has been identified causing unreliable operation or overloaded elements. - An Emergency Notice must be declared by ERCOT before Zonal Techniques may be utilized - Post a message on the MIS Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to help control the [zone – zone] CSC” |
| NOTE: | Zonal limits may change due to an outage cancellation, extension of an outage, or the early completion of an outage. |

# 2.2.7 	West - North Dynamic Stability Limit

Procedure Purpose: To maintain West to North stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | If the West-North Stability limit calculated on the spreadsheet changes value or color, update the RTMONI limit on the “Stability-WN” monitor to the value shown on the spreadsheet. |
| 2 | If the monitored flow on the Stability-WN monitor is approaching 85% and wind is climbing: - Activate the West – North OC1 - Change the W-N CSC limit to the Stability limit in RTMONI to give transparency to the Market. - Post a message on the MIS: Typical Script: “ERCOT is controlling the West - North Dynamic Stability Limit with the West – North OC1”. |
| 3 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - OOME/VDI wind down - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control the West to North dynamic stability limit.” |
| 4 | If Wind Generation Resources in the McCamey Area are utilized follow procedure: 2.2.14 Managing Generation Resources in McCamey Area. |
| NOTE: | If Zonal Techniques failed to control the West-North Stability limit and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |

# 2.2.8 	North-Houston Dynamic Stability Limit

Procedure Purpose: To maintain North to Houston stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | VSAT should be checked at least every hour, or more frequently as necessary. If North-Houston 345kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. |
| 2 | Determine if the Reliability margin is within 200MW of the Reliability margin: - O-HOUS_L – 400 MW - N-H G – 400 MW - N-H L – 400 MW If the value is within 200MW of the Reliability margin: - Request TSP’s in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| 3 | Determine if the Reliability margin is at or below the Reliability margin: - O-HOUS_L – 200 MW - N-H G – 200 MW - N-H L – 200 MW If limit value is at or below the Reliability margin: - Activate the North – Houston OC1 - Change the North – Houston CSC limit in RTMONI to the N-H VSAT Transfer Limit located in VSAT for Market transparency. - Post a message on the MIS: Typical Script: “ERCOT is controlling the North - Houston dynamic stability limit with the North – Houston OC1”. |
| 4 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - Fleet up in Houston area - Utilize quick start units in the Houston area - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control North – Houston dynamic stability limit.” |

# 2.2.9 	OC1 Limits for Outage Support

Procedure Purpose: Adjusting OC1 limits to support an outage.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Adjust OC1 limits as required to support an outage. - If flow across a CSC is already below the limit required to support an outage, then it is permissible to wait and adjust the OC1 limit at the scheduled start time of the outage. - IF flow across a CSC is above the limit required to support an outage, then adjust the OC1 limits for intervals proceeding the scheduled outage start time such that flow across the constraint is gradually reduced to at or below the limit required to support the specific outage. - While this action might result in over-constraining for a brief period, it is preferable to the negative effects of a sudden reduction in the OC1 limit. |
| NOTE: | If step 1.2 is required, use the MIS and post that ERCOT is controlling to a limit other than the one posted. Typical Script: The “CSC Name” limit will change to “MW Amount” at “Time”. ERCOT will start controlling to this limit in accordance with Section 2.2.6 of the Transmission Security Desk procedures. |
| 2 | When a CSC limit changes, immediately change the limit in RTMONI. Record this event in the Transmission Security log. |

# 2.2.10 	Pre-Contingency Action Plans

Procedure Purpose: To implement a Pre-Contingency Action Plan.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| CAUTION: | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability. |
| 1 | When RTCA shows a post-contingency overload and a PCAP exists to resolve it, - REVIEW the PCAP with the associated Transmission Operator. - Notify the Shift Supervisor of the anticipated actions. |
| 2 | Direct the execution of the PCAP with the associated transmission operator: Typical script: “This is ERCOT operator [first and last name]. ERCOT is requesting [TO] to implement the **** PCAP and [open/close] [breaker(s)]. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 4 | Between 0000 and 0500 each day, the Transmission & Security Desk Operator should review the logs and verify that no PCAP remain in effect from the preceding day. IF any PCAPs are still in use, evaluate system conditions to determine if: - The PCAPs should remain in effect, OR - The system should be returned to a normal status. |
| 5 | IF the ERCOT System Operator and Shift Supervisor agree that the PCAP is no longer needed, the Transmission & Security Desk Operator shall direct the TO to: - Return the system to its’ normal status, OR - Return the system to its’ status prior to implementation of the PCAP Which ever state is applicable. |

# 2.2.11	SPS Intervention

Procedure Purpose: To monitor and prevent an SPS operation if possible.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | If notified to take a SPS in/out of service, ensure OPS Planning is notified. |
| NOTE: | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE: | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingent loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario congestion management is not be needed until the criteria in Desk Top Guide Section 3.3 is met. |
| NOTE: | Special Protection Schemes (SPS) - EXAMINE the results in RTCA for SPS activation. - If “SPS” is identified as a post contingent overload, EXAMINE the color of the background. - Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |
| NOTE: | Typically SPS’s are to solve post-contingent overloads on the Transmission System. Due to outages, either (Planned or Forced) the Transmission topology is changed temporarily. During these conditions the ERCOT Transmission & Security operator(s) will utilize Congestion Management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 1 | Monitor the Excel spreadsheet “Real Time Values” - Each SPS will be displayed, as the SPS activation threshold increases the display changes colors - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 2 | If the system operator receives a call from a TSP or as the threshold increases on the SPS to greater than 90%, then congestion management techniques should be employed in an attempt to prevent its’ activation. |
| NOTE: | If an SPS operates refer to procedure: - 2.1.4 OOME – VDI Guidelines |

# 2.2.12  	Remedial Action Plans

Procedure Purpose: To implement a Remedial Action Plan.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | A Remedial Action Plan (RAP) is designed to relieve the loading on the Transmission Facility within 15 minutes. ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the 15-Minute Rating. The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within 15 minutes. The “15-Minute Rating” and “LDSH” refer to the same thing. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |

# 2.2.13 	Mitigation Plans

Procedure Purpose: To implement a Mitigation Plan.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. If necessary, continue to use congestion management methods for post contingency loading after initiating the MP. With a MP, an operator does not need to declare a Watch for a post contingency overload. If a MP is enacted and subsequent congestion management techniques do not control post contingency loading, ISSUE a transmission Watch. |
| CAUTION: | MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |
| 1 | When RTCA shows a post-contingency overload greater than 100% of the Emergency Rating, attempt to resolve the overload by using congestion management methods. |
| 2 | If congestion management methods do not work, review the MPs to determine if an action plan exists for this overload condition. |
| 3 | If a MP exists If a MP exists for this contingency: - Review the Mitigation Plan with the associated Transmission Operator - [TO] repeats back directive to verify the plan is understood. - Notify the Shift Supervisor of the anticipated actions. |
| 4 | IF a MP does not exist for this contingency and the Outage Notes do not provide a plan, REQUEST (as time permits) that Operations Engineering investigate development of a MP. |
| 5 | If the contingency anticipated by the MP takes place: - DIRECT implementation of the MP to the Transmission Operator - [TO] repeats back directive to verify implementation is understood. - RESPOND as quickly as possible to requests made by the Transmission Operator in accordance with the MP If necessary, continue to use congestion management methods for post contingency loading after initiating the MP. |
| 6 | When the contingency clears, notify the TO as soon as possible. |

# 2.2.14 	Managing Generation Resources in McCamey Area

Procedure Purpose: To maintain stability of the wind powered generation in the McCamey area.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Rapid Response Wind Farms (RRWF) are designated as such under the Wind Unit Limitations located at the following link. All other units on the list are Slow Response Wind Farms (SRWF): https://tcr.ercot.com/default.cfm?func=tcrpostings |
| NOTE: | In real time operations, “Total Transmission Capacity” and “Maximum output allowed by system conditions” refers to RTCA or RTNET study results. Slow Response Wind Farms can respond to ERCOT Dispatch Instructions no more often than one instruction per three consecutive hours. The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. McCamey area wind generation will use VDIs to set initial wind limits prior to the operating day. |
| 1 | Use the wind limits from the “Transmission Limits to be Monitored” sheet developed by the Operations Engineers on the VDIs. |
| 2 | RRWF are allowed to operate above their daily limits. If operating above their limits is causing system problems, then call the RRWF and ask them to come back to their daily limit |
| 3 | If the Total Transmission Capacity in the McCamey area is less than the total amount of “Wind Unit Limits” allocated to both SRWF and RRWF, THEN: 3.1 Instruct the RRWFs to reduce output such that the congestion is relieved. This instruction should be for a minimum of one (1) hour duration (constitutes 4 consecutive 15-minute intervals). - 3.2 On the fifth interval, instruct each SRWF to reduce its output by 10 Mw for a minimum of three hours. - 3.3 After each SRWF has reduced its output by 10 MW, and system conditions permit, the RRWF dispatch instruction can be released. |
| 4 | At least three hours after performing Step 3.2 above, and if system conditions permit, perform step 4.1, otherwise perform 4.2 4.1 Resume operation of the SRWFs up to an output level that will allow RRWF to operate at or above their “Wind Unit Limits” ownership levels. OR 4.2 Dispatch both SRWF and RRWF to levels that will allow them both to operate to the maximum allowed based on capacity-ratio-share. (Refer to the calculation tab on the Real-Time Values spreadsheet to calculate the capacity-ratio-share) |

# 2.2.15 	Managing Line Rating Changes

Procedure Purpose: To obtain information on changes in line ratings.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | When notified by a Transmission Operator of a line rating that is different from the ratings currently in RTNET, obtain the following information from the Transmission Operator: - Equipment ID Name - MVA ratings (Continuous, Emergency, and 15 Minutes) - Name of Operator on duty - Name of Transmission Operator (Company) - Name of Transmission Operator’s authorizing engineer - Authorizing engineer’s contact phone number |
| 2 | Continue to operate according to RTNET ratings. - Provide this information to the Shift Supervisor - Enter this information in the Transmission log under the “Line Rating Changes” log type |

# 2.3 Manage Outages

# 2.3.1 	Approval of Outage on Transmission Devices Less than One Hour

Procedure Purpose: To obtain information for outages on transmission devices that will be less than one hour in duration.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/01/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | RECEIVE verbal request for permission to remove a transmission device from service for less than one hour. |
| 2 | Through discussion with a Transmission Operator, verify that the work being done will not prevent the device from being placed back in service immediately. |
| 3 | As time permits, determine through knowledge of present real-time operation or security analysis that such operation will not affect the reliability of the Transmission System. |
| 4 | Verbally approve for the Transmission Operator to remove a transmission device from service for less than one hour. |
| 5 | Log appropriate data in Transmission & Security log. |

# 2.4.3 	Voltage Security Assessment Tool (VSAT)

Procedure Purpose: To monitor system conditions and prevent voltage collapse.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure 2.2.8 North-Houston Dynamic Stability Limit. |
| NOTE: | VSAT should be checked at least every hour, or more frequently as necessary. |
| NOTE: | To contact VSAT support, check the board in the back of TCC for the on-call personnel. |
| 1 | Determine if VSAT has run in the last 80 minutes. Reference Display: Network Online Sequence - If VSAT has not run in the last 80 minutes, contact VSAT support. - IF a South-Houston or North-Houston 345 kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. Otherwise, continue with following steps. - If any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below, it is suggested to manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) more frequently than the periodic scheduled VSAT run and proceed to step 2. Otherwise, continue with the following steps. Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. |
| 2 | Confirm that VSAT is indicating either “Normal” or “Pending” status. NOTE: If VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status, contact VSAT support. Reference Display: Network Online Sequence |
| 3 | With VSAT in “Normal” status, determine if it indicates that a Reliability Margin may be exceeded. Reference Display: VSAT Results Page |
| NOTE: | If one of the Comanche Peak units is forced or planned to be offline, there must be at least two sizeable DFW area units online at all times (along with the one Comanche Peak unit online). |
| NOTE: | If VSAT does not indicate a Reliability Margin is below the Reliability Margin, no further action is required. |
| 4 | Determine if the Reliability margin is less than the value located in the table below. Reference Display: Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200Mw. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. If the VSAT Reliability margin value is less than the Reliability margin value posted: |
| 5 | Check to see if the same contingency is unsolved in RTCA. Reference Display: Contingency Analyst Solution Results If so, call VSAT support and proceed to Step 7. If not, call VSAT Support for verification and weak bus information. |
| 6 | Request the TSP in the affected area turn on capacitor banks and turn off reactors near the weak busses. |
| 7 | OOME fast ramp generators to increase generation in weak bus area. If all the online units in the weak bus area are running at maximum capacity, OOMC units that are available but offline (in weak bus area). |
| 8 | Rerun VSAT with new information. Reference Display: Network Online Sequence |
| 9 | Determine if the Extra-Interface Limit pre-contingency is greater than the Reliability margin value located in the table below. Reference Displays: VSAT Results Page Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. NOTE: If the Extra-Interface Limit pre-contingency value is greater than the Reliability margin value, no further action is required. If not, proceed to Step 12. |
| 10 | If necessary, contact VSAT Support and have them verify the the results from the VSAT application on the weak bus information. |
| 11 | If it was determined that VSAT results were not an actual problem. No further action is required and the system may be restored back to the original state. |
| 12 | Determine if there are more units available in the affected area. If there are more units available in the affected area, repeat steps 6, 7, 8, and 9. |
| NOTE: | If there are no more units available in the area, proceed to step 13. |
| 13 | Ensure that the OPS Support Engineering group has been contacted to devise a mitigation plan. |

# 2.5	Emergency Operations

# 2.5.1	Issue an Operating Condition Notice (OCN)

Procedure Purpose: To inform the Market Participants of a system Operating Condition Notice.

| Protocol Ref. | 5.6.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.1 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE an Operating Condition Notice (OCN) IF: - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - There is the potential for icing conditions to affect major transmission systems. - There is a projected capacity shortage or insufficient balancing bids. - Wet weather, such as a tropical storm making land fall. |
| 2 | Issuance of an OCN requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Using the Hotline, notify all TOs of OCN. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an OCN for [state OCN]. [TO] please repeat this back to me. That is correct, thank you.” |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.2	Issue an Advisory

Procedure Purpose: To inform the Market Participants of an Advisory.

| Protocol Ref. | 5.6.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.2 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE an Advisory IF: - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the “National Hurricane Center” http://www.nhc.noaa.gov/ - When ERCOT recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - When weather or ERCOT System conditions require more lead-time than the normal Day Ahead market allows. - Transmission system conditions indicate ERCOT is likely to exceed established limits and no practicable resource solution exists - Loss of communications or control condition is anticipated or significantly limited - Adjusted Responsive Reserve drops below 3000 MW - When long-range notice (approximately 48 hours) is needed to ensure the secure operation of the ERCOT system, alert the Market Participants to a potential threat to reliable operations with the following: - Lead time for dual fuel generating units to prepare for fuel supply problems in the event of anticipated severe cold weather - Any other operational concerns |
| 2 | Issue an Advisory: - Post on the ENS - Post on the MIS - Notify TOs via the Hotline |
| 3 | Using the Hotline, notify all TOs of Advisory. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory for [state Advisory]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.3	Issue a Watch

Procedure Purpose: To inform the Market Participants of a Watch.

| Protocol Ref. | 5.6.5 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.3 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits with no practicable resource solution - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition - There is a hurricane in the Gulf with expected landfall in Texas - A cold front has arrived with temperature anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - Forced Outages or other abnormal operating conditions occur with no practicable resource solution - Adjusted Responsive Reserve drops below 2500 MW |
| 2 | Issuance of a Watch requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Before issuing a Transmission Watch for transmission issues, notify the TO and discuss the actions you are about to take. |
| 4 | When issuing a Watch for a transmission issue, use the following script for making the hotline call: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission Watch due to the outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” Note: If the facility outage is a generator state “a generating unit”. |
| 5 | MIS and ENS posting script: ERCOT issued a Transmission Watch due to the outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” |
| 6 | When issuing a Watch for other reasons, use the following script for posting the message and making the hotline call: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.4	Issue an Emergency Notice

Procedure Purpose: To inform the Market Participants of an Emergency Notice.

| Protocol Ref. | 5.6.6 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.4 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A transmission condition has been identified that requires emergency energy from any of the South DC-Ties. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no practicable resource solution exists. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability |
| 2 | Issuance of an Emergency Notice requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Before issuing an Emergency Notice for transmission issues, notify the TO and discuss the actions you are about to take. |
| 4 | When issuing an Emergency Notice for a transmission issue, use the following script for making the hotline call: Typical Script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice due to the outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” Note: If the facility outage is a generator state “a generating unit”. |
| 5 | MIS and ENS posting script: ERCOT issued an Emergency Notice due to the outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” |
| 6 | When issuing an Emergency Notice for other reasons, use the following script for posting the message and making the hotline call: Using the Hotline, notify all TOs of the Emergency Notice. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.6	 Implement EEA

Procedure Purpose: To implement an Energy Emergency Alert(s) for the appropriate system conditions.

| Protocol Ref. | 5.6.6.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.5.3.2 |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA. EEA in this procedure is to be implemented in concert with the Frequency Control Desk EEA procedures. Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted TOs should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaR as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any level of EEA is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| 1a | Implement EEA 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 1b | Using the Hotline, notify TOs to implement EEA 1. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA1. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 1 |
| 2a | In addition to measures associated with EEA 1; Implement EEA 2A IF, - EEA 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 2b | Using the hotline, notify TOs to implement EEA 2A. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2A; - LaaRs are being deployed - If local operating conditions permit, TOs are to reduce customer loads by using distribution voltage reduction measures - Report back to ERCOT when these actions have been initiated and/or completed [ TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2A |
| 2e | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures that have been taken. |
| 3a | In addition to measures associated with EEA 1 & 2A; Implement EEA 2B IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. If no EILS exist, skip EEA 2B and proceed to EEA 3 if needed |
| NOTE: | Unless a media appeal is already in effect, one is required in this level. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation. Notify TOs that a media appeal for voluntary energy conservation is in effect via Hotline. |
| 3b | Using the hotline, notify all TOs to implement EEA 2B. - When TOs have answered the Hotline, print the Hotline log Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2B. EILS are being deployed. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2B |
| 4a | In addition to measures associated with EEA 1, 2A & 2B; Implement EEA 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available |
| NOTE: | Firm load is to be shed in 100 MW blocks. TOs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TSPs shall not manually drop load connected to under-frequency relays during the implementation of EEA. |
| 4b | Using the hotline, notify TOs to implement EEA 3. - When TOs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 3. ERCOT is instructing all Transmission Operators to shed their share of <amount> MW. Transmission Operators are to report to ERCOT when this is complete and give the amount of load shed. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4d | Instruct the Frequency Control Desk Operator to inform the QSEs via the Hotline that firm load is being shed. |
| 4e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 3 |
| 4f | Verify and log the following as appropriate: - Block Load Transfers (BLTs) have been implemented as appropriate. - Distribution voltage reduction measures have been taken where possible - Load shed instructions have been received and enacted. |

## 2.5.7	 Restore EEA Steps

Procedure Purpose: Backing out and terminating Energy Emergency Alert(s).

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA Restoration. EEA in this procedure is to be implemented in concert with the Frequency Control Desk EEA procedures. |
| 4a | Restore firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MW |
| 4b | Using the hotline, notify TOs of firm load restoration. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is instructing all Transmission Operators to restore their share of <amount> MW leaving <amount> MW still off. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load restored. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4d | Ensure the following is posted on the ENS and MIS: - “ERCOT is restoring firm load” |
| 4e | Maintain Adjusted Responsive Reserve supplied from generation equal to 1150 MW while restoring firm load. |
| 4f | Ensure that the Frequency Control Desk Operator notifies the QSEs that firm load is being restored. |
| 4g | Move from EEA 3 to EEA 2B when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MW, AND - All firm load has been restored |
| 4h | Using the hotline, notify TOs of the reduction from EEA 3 to EEA2 B - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B, LaaRs are going to be recalled. Go back to normal, if distribution voltage reductions were made. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings |
| 4i | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4j | Ensure the following is posted on the ENS and MIS: - EEA 3 to EEA 2B |
| 3a | Move from EEA 2B to EEA 2A when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MW, AND - All LaaRs have been recalled, AND - Sufficient Regulation Services exists to control to 60 Hz. |
| 3b | Using the hotline, notify TOs of the reduction from EEA 2B to EEA 2A: - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - EEA 2B to EEA 2A |
| 3e | Appeal through the public news media for voluntary energy conservation may be terminated, notify Shift Supervisors |
| 2a | Move from EEA 2A to EEA 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW, AND - All LaaRs have been restored, or replaced with generation. |
| 2b | Using the hotline, notify all TOs of the reduction from EEA EEA 2A to EEA 1: - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1, all EILS are being recalled, [if Block Load Transfers have been executed please coordinate with ERCOT to restore them as system conditions permit.] [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - EEA 2A to EEA 1 |
| 1a | Move from EEA 1 to EEA 0 when: - EILS resources have been recalled. AND - All uncommitted units secured in EEA 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exists to control to 60 Hz. |
| 1b | Using the Hotline, notify TOs of the reduction from EEA 1 to termination: - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is terminating EEA. A Watch still remains in effect. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - EEA termination |

## 2.5.9	 Restoration of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by Transmission and Security Desk Operator at the Back-up Control Center (BCC) in restoring Real-Time operations.

- Additional staff has arrived, including a Shift Supervisor,

- BCC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: 05/20/09 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Prior to Resuming Congestion Management | Upon arrival to the BCC: - Check with the Frequency Control Desk Operator to find out about any calls received from TOs and if any VDIs were issued, - Check with Operating Period Desk Operator to find out if RTBM deployments have resumed. |
| Market Notification | When you are ready to resume normal operation, place the following Hotline call to the TOs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT is resuming normal, Real-Time operations from the back-up control center. Until further notice, direct all Transmission and Security related phone calls to (512) 225-7130.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |