## Power Operations Bulletin # 421

ERCOT has revised the Frequency Desk Procedure Manual.

The specific changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.2.3 	Monthly Testing of Satellite Phone System

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R2 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in Section 7 of the Desktop Guide for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Section 7 of the Desktop Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form. An electronic copy of this form is located in P:\ SYSTEM OPERATIONS “Satellite Bridge Testing forms” folder. |
| 4 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the form is complete. |
| 5 | Log the test date and results in the ERCOT Operations Log. |
| 6 | When working out of the Back-up during the monthly scheduled dates, test at least one Satellite phone. If any problems are encountered, followed step 7. |
| 7 | Verify with the Shift Supervisor that the following personnel are notified for any Satellite phone problems during the test by e-mail: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |

# 2.4.1 	Monitor SCE for each QSE

Procedure Purpose: To ensure that QSE’s Schedule Control Error is maintained within acceptable limits and the telemetry is working correctly.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R1.6 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Compare QSE’s SCE with the ERCOT calculated SCE. If these two values differ significantly, and the cause is not already known, review SCE components with the QSE to determine the source of the disagreement. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 2 | When the source of disagreement is established, decide which end (QSE or ERCOT) is most likely in error. If the error is on the ERCOT end, call technical support if appropriate. If the error is on the QSE end, request that the QSE take corrective action. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 3 | If SCE for a QSE departs significantly from 0 for an unknown reason, or if a SCE violation is causing a reliability problem, call the QSE involved and determine the reason for the deviation. |
| 4 | If a wind only QSE SCE deviates significantly from 0 call the QSE and requested that they update their resource plan and base power schedules. The resource plans and base power schedules should be updated together and stay matched. Since base power changes are not allowed during the operating hour the SCE can not be corrected immediately. |
| 5 | If the QSE is unable to correct the problem, notify the Shift Supervisor. |
| 6 | LOG in the Operator’s Log the event, including the QSE name, the name of the person communicated with, the date and time of the conversation, magnitude, length, reason for the deviation and any other pertinent information. |

# 2.5.5	 Response to High Frequency

Procedure Purpose: A process to alleviate a high frequency occurrence.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R11 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
|  | The following steps are to be taken in the event of High system frequency of unknown cause. If the cause of High system frequency is known and system response or other actions are expected to correct it, then the following steps are optional. |
| NOTE: | The Frequency Control Desk Operator may consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. |
|  | Frequency above 60.05 and continuing to climb or over 60.05 > five minutes. |
| 1 | If regulation down service remains and is deploying: - Call QSEs with positive SCE and direct them to reduce generation to return their SCE to zero as soon as possible. - Remove SCE feedback from QSEs with high SCE and monitor frequency response. |
|  | Frequency above 60.10 and continuing to climb |
| 2 | If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE within five (5) minutes or no QSE appears to be hanging out or no physical regulation down service is available: Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain 0 SCE) to reduce generation. Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#] to [QSE]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this back to me. That is correct. I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Once regulation is restored and frequency is stable, end fleet down generation instruction: Typical script: This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time]. This ends the fleet down instruction. Please repeat this back to me. That is correct, thank you.” |
| 4 | Log the actions that were taken and forward completed VDI(s) to Shift Supervisor, as time permits. |

## 2.5.6	 Response to Frequency Decay

Procedure Purpose: Response to severe frequency decay, up to and including, using EEA 2A and the deployment of LaaR.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 R2.4 | EOP-002-2 R5 & 6.1 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | UFRs will deploy as follows: Hydro RRS - 59.90 Hz RRS LaaR – 59.7 Hz |
| 1 | If Regulation Service is depleted, AND frequency is below 59.97 Hz and continues to decay, implement the following actions as necessary: - Ensure any remaining Balancing Energy is deployed. - ISSUE a Fleet VDI to the QSE(s) showing the highest amount of spinning reserves available. - When issuing the VDI, the operator should request enough generation to restore frequency and recall approximately 50% of Regulation Up Service. |
| 2 | VERIFY that the Balancing Offset is set to an approximate value that will restore Regulation Service. |
| 3 | IF frequency continues to decay, ENSURE 33% of the TOTAL Responsive Reserve Service is deployed (approximately 760 MW). |
| NOTE: | On depletion of the first 33% of TOTAL Responsive Reserve, ERCOT shall declare an EEA in effect (Protocols Section 6.7.3). |
| 4 | IF Step 3 of this procedure does not arrest the frequency decay AND frequency reaches 59.85, IMPLEMENT EEA 2A and deploy ALL LaaR bid to supply Responsive Reserve. |
| 5 | Follow EEA Procedures as required per section 2.6.6. |
| NOTE: | Verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| NOTE: | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency Refer to procedure 2.5.3 for Actions When Frequency Telemetry is Incorrect. |

## 2.5.7 Potential DCS Event – Use of LaaRs to Arrest a Frequency Disturbance

Procedure Purpose: To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 R2.4 & R6.2 | EOP-001-0 R5 | EOP-002-2 R5 & 6.1 |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | There are times when the MW amount lost will be more than the NERC reportable amount. In these cases LaaRs will still need to be used to recover frequency |
| NOTE: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than scheduled frequency prior the disturbance. Within 90 minutes ERCOT shall fully restore its Contingency Reserves to the pre-contingency level. This 90 minute restoration period begins at the end of the disturbance recovery period. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1083 MW OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1083 MW. It is anticipated that the deployment of LaaRs will occur in stages. LaaRs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, a text message may be sent as time permits so as not to impede system operations. In order to control frequency, be prepared to issue a “Fleet Down” VDI once the system has recovered to its scheduled/pre-disturbance frequency value. |
| 1 | When a low frequency disturbance occurs due to a loss of generation, DETERMINE immediately, by calculating the loss of generation, if the event is potentially a NERC Reportable DCS Event. |
| 2 | If a low frequency disturbance occurs, AND there is NO indication of a generation loss, determine the magnitude of the event by using the “Filtered ACE Incremental MW Requested” tag, assume that a potential DCS event has occurred and SCADA communications has been lost if the total generation loss is greater than 1000 MW, implement Step 4 of this procedure. - Determine the magnitude of the event by using the “Filtered ACE Incremental MW Requested” tag on the “ERCOT & QSE Summary Page” in PI. - Take care to calculate the entire generation loss from the PI tag, not just the difference between zero and the lowest number. Example: If the “Filtered ACE Incremental MW Requested” pre-disturbance value is +150 MW, and post disturbance value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. |
| 3 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 4 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - When system conditions warrant, issue a VDI using the hotline instructing QSEs to deploy ALL un-deployed LaaRs and hydro generation that are bid to supply Responsive Reserve. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs and instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Verbal Dispatch Instruction instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct; I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Ensure printed Hotline Log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 6 | Complete the VDI form (See Desk Top Guide Section 7.4) and process. - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows: “All QSEs are required to deploy any un-deployed LaaRs and hydro supplying Responsive Reserve due to a potential DCS event.” |
| 7 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being deployed. |
| NOTE: | verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| 8 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being restored. |

## 2.5.8	 Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-003-2 R2 | IRO-005-1 R1.1 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: Page 1: 345 KV Transmission Equipment Status Page 2: 138 KV Transmission Equipment Status Page 3: Generator Breaker Status Page 4: Transmission Line Overloads and Voltage Violations- critical alarms Page 5: Generator Unit, QSE SCE, and ERCOT ACE Status Page 6: RTNET Status Page 7: ICCP Status Page 8: EMS Task Application Alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 5, 6, and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Transmission & Security Desk to clear the alarms approximately every 2 to 3 hours or as needed. |

## 2.6.6	 Provide Advance Notice of Diminishing Responsive Reserve

Procedure Purpose: Guidelines for issuing advance notice of diminishing Responsive Reserves

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 R2.4 | EOP-001-0 R3.1 | EOP-002-2 R1, R2, R4 & R6.1, R6.2, R6.4, R8 | IRO-005-1 R1.4, R1.5, R4 |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory has been issued. |
| 4 | Ensure the following is posted on the ENS and MIS: - Advisory issued for ARR below 3000 MW. |
| 5 | When adjusted Responsive Reserve falls below 2500 MW: Using the Hotline, notify QSEs: - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. - Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. - Suspend all ERCOT required generation unit testing. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure Non-Spin has been deployed. |
| 7 | OOME to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0. Follow up with a Settlements only VDI stating :OOMC for Quick-start” on the VDI form. |
| 8 | Instruct the Transmission & Security Desk Operator to notify the TOs that a Watch has been issued. |
| 9 | Ensure the following is posted on the ENS and MIS: - Watch issued for ARR below 2500 MW. |

## 2.6.7	 Diminishing Reserve Notice Cancellation Guidelines

Procedure Purpose: To provide notifications and back out of the actions taken during diminishing system reserves.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS. |
| 1 | IF Non-Spin has been deployed, work in conjunction with the Operating Period Desk Operator to recall Non-spin Reserve Services as system conditions permit. |
| 2 | As system conditions permit, recall/release incrementally, any additional generation that was brought online to recover ARR. |
| 3 | Cancel a Watch or Advisory when: - All related OOM and Non-spin deployments have ended, AND - ARR is >= 3200 MW, AND - Load is trending down, OR - The Excel MAI shows the “Max Cap Room” increasing over the next two hours |
| 4 | . IF a watch has been canceled, - NOTIFY QSEs that testing may be resumed. Typical scripts: Cancel Advisory - “This is ERCOT operator [first and last name]. ERCOT is canceling the Advisory for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 3000 MW. [QSE] please repeat this back to me. That is correct, thank you.” Cancel Watch - “This is ERCOT operator [first and last name]. ERCOT is canceling the Watch for Adjusted Responsive Reserves. Adjusted Responsive Reserves are now above 2500. MW. At this time, performance testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 6 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory or Watch has been cancelled. |

## 2.6.8	Implement EEA

Procedure Purpose: To implement an Energy Emergency Alert(s) for the appropriate system conditions.

| Protocol Ref. | 5.6.7 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.5.3.2 |  |  |  |
| NERC Std. | COM-002-2 R2 | EOP-001-0 R3.1, R3.3 & R5 | EOP-002-2 R1, R2, R4 & R6.1, R6.2, R6.4, R6.6, R8 | IRO-005-1 R1.5, R1.10 |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Frequency Control Desk will implement applicable levels of the EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s should be notified via Hotline call. For the purpose of this procedure, Physical Responsive Capability PRC plus Responsive Reserve Service (RRS) provided from LaaR as defined and used in the ERCOT Operating Guides Section 1.6 and 4.5.3.3 shall be referred to as Adjusted Responsive Reserves. |
| NOTE: | Whenever the QSE or TO hotline is used to issue an Emergency Notice that any level of EEA is being implemented, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the directive and direct them to repeat back again. Continue until an acceptable repeat back is received. |
| NOTE: | IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3 |
| 1a | Implement EEA 1 IF: - Adjusted Responsive Reserves fall below 2300 MW, OR - ERCOT has deployed over 760 MW of Responsive Reserve Service (RRS) supplied from generation resources in response to low frequency due to a capacity insufficiency. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 1b | Using the hotline, notify QSEs to implement EEA 1. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 1, QSEs are to do the following: - Report when online available capacity is at risk due to adverse circumstance. - Immediately and continually update Resource Plans to reflect all resource delays and limitations should they occur. - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency. - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - Suspend testing on all resources. - QSEs are to report back to the ERCOT System Operator on the progress and/or completion of the aforementioned items. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 1 |
| 1e | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources |
| 2a | In addition to measures associated with EEA 1 Implement EEA 2A IF: - EEA 1 fails to maintain Adjusted Responsive Reserves equal to or greater than 1750 MW. Reference Display: Generation Area Status, Generation Reserve Status, Available Details, ERCOT ON UNIT ERCOT Load Acting As Resource (LaaR) |
| 2b | Using the hotline, notify QSEs to implement EEA 2A. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2A; ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to QSEs to deploy all LaaRs bid to supply Responsive Reserves Service within ten (10) minutes. Also: - QSEs are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. - QSEs are required to report back to the ERCOT System Operator when this task has been completed. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that LaaR have been deployed. |
| 2d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2A |
| 2f | VERIFY and log the following as appropriate: - Available Non-Spin has been deployed - Available uncommitted units have been dispatched and loaded as necessary - Testing has been suspended on all resources. - LaaRs have been deployed. |
| NOTE: | Unless a media appeal is already in effect, one is required in this level. Ask the Shift Supervisor about the issuance of the media appeal for voluntary energy conservation |
| 3a | In addition to measures associated with EEA 1 & 2A; imPLEMENT eEA 2B IF: EILS has been procured AND any of the following occur: - Frequency drops below 60.00 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available - Based on a combination of system conditions, the operator believes that an EILS deployment is necessary to maintain frequency at 60.00 Hz. If no EILS exist, skip EEA 2B and proceed to EEA 3 if needed. |
| 3b | Using the hotline, notify QSEs to implement EEA 2B. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 2B. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSE’s to deploy contracted EILS Resources in the current time period until further notice. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Instruct the Transmission & Security Desk Operator to inform the TOs via the Hotline that EILS Resources have been deployed. |
| NOTE: | EILS Resources have 10 minutes to comply with this instruction. If conditions develop that require implementing EEA 3, ERCOT may at its discretion shed firm load prior to the expiration of the 10 min. period. When a deployment of EILS is implemented and the event is still in effect when one Time Period ends and the other begins, deployed EILS Resources will remain deployed until, at ERCOT’s discretion, they are recalled via a Hotline call to QSEs. ERCOT System Operators will make reasonable efforts to recall EILS Resources that are no longer obligated due to the expiration of a Time Period. |
| 3d | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3e | Ensure the following is posted on the ENS and MIS: - Implemented EEA 2B |
| 4a | In addition to measures associated with EEA 1, 2A, & 2B; Implement EEA 3 IF: - Frequency drops below 59.80 Hz, OR - Frequency begins to trend down with no indication for recovery, OR - Adjusted Responsive Reserves continue to trend down, OR - Adjusted Responsive Reserves are no longer available. |
| 4b | Using the hotline, notify QSEs to implement EEA 3. - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is implementing EEA 3. Transmission Operators have been instructed to shed <MW Amount> of firm load. QSEs confirm that their generation resources are at maximum output. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 4d | Ensure the following is posted on the ENS and MIS: - Implemented EEA 3 |
| 4e | VERIFY the following: - All Generation Resources are at full capacity - Available Non-Spin has been deployed - Uncommitted QSE’s available units have been dispatched to full load - All resource testing has been suspended - All LaaRs have been deployed by QSEs with RRS Obligations - All EILS Loads have been deployed by QSEs with EILS Obligations |

## 2.6.9	Restore EEA

Procedure Purpose: Backing out and terminating Energy Emergency Alert(s).

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Frequency Control Desk will implement applicable levels of the EEA Restoration. Numbering of procedure steps is reversed to coincide with EEA. EEA in this procedure is to be implemented in concert with the Transmission & Security Desk EEA procedures. |
| 4a | Restore firm load when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is greater than 1150 MW |
| 4b | Notify the QSEs when the Transmission & Security Desk Operator begins to restore firm load. Using the hotline, notify QSEs of the restoration of firm load: - When QSEs have answered the Hotline, print the Hotline log Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is currently restoring firm load. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4c | Move from EEA 3 to EEA 2B when: - Sufficient Regulation Service exist to control to 60 Hz, AND - Adjusted Responsive Reserve supplied from generation is equal to 1150 MWs, AND - All firm load has been restored. |
| 4d | Using the hotline, notify QSEs of the reduction from EEA 3 to 2B, if 2B was skipped move from EEA 3 to 2A : - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B.” QSEs that deployed LaaR in EEA 2A may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4e | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 4f | Ensure the following is posted on the ENS and MIS: - EEA 3 to EEA 2B |
| 4g | Instruct the Transmission & Security Desk Operator to notify the TOs that LaaRs are being restored. |
| NOTE: | Maintain a minimum of 1150 MWs of Adjusted Responsive Reserve supplied from generation resources while LaaRs are being restored |
| 3a | Move from EEA 2B to EEA 2A when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 1750 MWs, AND - All LaaRs have been recalled. AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 3b | Using the hotline, notify all QSEs of the reduction from EEA 2B to EEA 2A: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3c | Ensure printed Hotline log has date, time, and reason for call information and forward to Shift Supervisor, as time permits. |
| 3d | Ensure the following is posted on the ENS and MIS: - EEA 2B to EEA 2A |
| 3e | Instruct the Transmission & Security Desk Operator to notify the TOs that ERCOT moved from EEA 2B to EEA 2A. |
| 3f | Appeals through the public news media for voluntary energy conservation may be terminated, notify Shift Supervisor |
| 2a | Move from EEA 2A to EEA 1 when: - The system can maintain Adjusted Responsive Reserve equal to or greater than 2300 MW AND - All LaaR have been requested to be restored or replaced with generation |
| 2b | Using the hotline, notify QSEs of the reduction from EEA 2A to EEA 1: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1. QSE’s that deployed EILS Resources in EEA 2B may begin to restore them at this time. [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 2d | Ensure the following is posted on the ENS and MIS: - EEA 2A to EEA 1 |
| 2e | Instruct the Transmission & Security Desk Operator to notify the TOs that EILS Resources are being recalled. |
| 1a | Move from EEA 1 to EEA 0 when: - EILS Resources have been requested to be recalled AND - All uncommitted units secured in EEA 1 can be released to reduce generation, AND - Emergency power from the DC Ties is no longer needed, AND - Sufficient Regulation Service exist to control to 60 Hz. |
| 1b | Using the hotline, notify QSEs of the reduction from EEA 1 to EEA 0: - When QSEs have answered the Hotline, print the Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is terminating EEA. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 1c | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 1d | Ensure the following is posted on the ENS and MIS: - EEA termination |
| 1e | Instruct the Transmission & Security Desk Operator to notify the TOs of the termination of EEA. |

## 2.6.10	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the Back-up Control Center (BCC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R5 | EOP-001-0 R4.4 | IRO-005-1 R1.10 |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC (cell phone or Emergency Power Fail (EPF) phones), THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the BCC - Notify them of the situation AND - Have them attempt to make contact with Security at TCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT is declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Issue a VDI to the QSE that was put on constant frequency, as time permits. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support, Telecommunications - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Most potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.6.11	Restoration of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Frequency Control Desk Operators at the Back-up Control Center (BCC) in restoring Real-Time operations.

- Additional staff has arrived, including a Shift Supervisor,

- BCC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | As additional Operators arrive, be sure to communicate any pertinent information that will assist them in getting their specific functions ready for normal operation. |
| Restoring Frequency Control | When an Operating Period Desk Operator has arrived, had time to get the offset calculation spreadsheet caught up, and is able to enter offset values into the MOI: IF: - Holding Real-time Balancing Energy Market (RTB) deployments, THEN: - Verify the proper operation of the RTB and that deployments are being sent to the Market Participants (MP) AND - Remove the QSE that is put on constant frequency. |
| Market Notification | IF: - RTBM is running and valid deployments are being sent, THEN: - Place the following QSE Hotline call: * * * WARNING * * * When removing a QSE from constant frequency control, remove ERCOT AGC from Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT is resuming normal, Real-Time operations from the back-up control center. Please continue to direct all phone calls to (512) 225-7100. ERCOT is ending VDI [#] at [time]. Resume with the [interval ending time] Balancing Energy deployments. [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Additional Notifications | Notify the following: - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations and/or designee - Engineering Support - These phone numbers have been programmed into the control room cell phone. |
| Notification of Additional Operators | WHEN: - All functionality has been resumed at the BCC, THEN: - Notify the additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System. |
| Contact Security | Notify Security that the transition of Operations to the BCC has been completed |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |

## 2.7.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005-2 R1 | INT-006-2 R1, R1.1, R1.2, R1.3 & R1.2 | INT-007-1 R1.1 & R1.2 | INT-009-1 R1 |
|  | TOP-002-2 R5, R9 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. |
| NOTE: | The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-tags are scheduled. |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: - Determine if the following information is correct on the E-Tag: - ERCOT is included as a Transmission Provider (TP) in the physical path. - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. - Determine if one or more E-Tags being submitted will cause the DC Tie to exceed the import/export limit for the tie. - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the import/export limit for the tie. - Call the PSE to have the E-tag modified, if modification is not done 20 minutes before the start of the ramp then; - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. - Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag was automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag was not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Summary Tag Validation Criteria Tag Approval Monitor - QSE Summary |
| 2 | The ramp rate for the Railroad DC-Tie will be 50 MW per minute due to reactive issues on the CFE side. Laredo and Eagle Pass DC-Ties will be ramped across a 10 minute window. - Ensure the ramp duration is filled out on Railroad E-Tags only - Laredo and Eagle Pass ramp duration will remain blank Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| 4 | ERCOT will allow QSE’s to submit E-Tags more than one (1) day in advance on the CFE DC-Ties. In these cases there will not be an associated schedule until the day-ahead. If a schedule is not received by 1400 in the day-ahead, notify the QSE and remind them that a schedule is needed. If the schedule is not received by 2000, curtail the E-Tag to zero. |
| 5 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

## 2.7.10	Emergency Energy across the CFE DC Ties

Procedure Purpose: Steps to secure emergency energy across the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R3.1, R7.2 & R7.3 | EOP-002-2 R1, R2 & R4 & R6.1, R6.2, R6.4 & R8 | INT-010-1 R3 | IRO-005-1 R4 |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must declare a Watch or an emergency and make the proper posting/hotline call when receiving emergency energy from CFE, whether it is for transmission issues or an EEA situation. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| NOTE: | If there are E-tags that can be curtailed to alleviate the emergency situation, referred to Procedure 2.7.6, Step 5. When notified by Hotline If in EEA situation, export E-tags should be curtailed first before emergency energy is received. |
|  | When notified by Hotline that ERCOT has implemented an EEA level, proceed with this procedure |
| 1 | When ERCOT is in need of the Emergency Energy: When notified by the Transmission & Security Desk of the need for emergency energy for a transmission issue or if in an EEA situation: - If there is import capacity room on the appropriate DC-Tie(s), contact AEP Corpus and request that they contact CFE to see if emergency energy is available - If emergency energy is available, determine the DC-Tie(s), MW amount, time and duration (if possible), - Request AEP Corpus to ramp the appropriate DC-Tie with the emergency energy - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Forward VDI(s) to Shift Supervisor (fax) as time permits |
| 2 | When CFE is in need of the Emergency Energy: The request will come from either the Transmission & Security Desk or AEP Corpus: - If there is export capacity room on the appropriate DC-Tie(s), coordinated with the Transmission & Security Desk to ensure it will not cause ERCOT transmission issues - With no issues, determine the DC-Tie(s), MW amount, time and duration (if possible) - Coordinate with Operating Period Desk - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Notify AEP Corpus to ramp DC-Tie(s) - Forward VDI(s) to Shift Supervisor (fax) as time permits |