## Power Operations Bulletin # 422

ERCOT has revised the Transmission & Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.1.2	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | If RTCA or the State Estimator has not solved within the last 20 minutes, refer to Desk Top Guide Section 3.1 and run through the checklist. If, after trying all the checks and RTCA and/or the State Estimator still has not solved, notify the on-call State Estimator Support Engineer and request the tool(s) be restored to operation as soon as possible. If RTCA will not solve but the EMS is available notify the on-call Operations Engineer to request limits be calculated manually. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 30 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to the ERCOT Transmission Operators: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 30 minutes. Please monitor your own service area and notify ERCOT when thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits when power flows reach 85% of their respective limits. Continue to monitor voltages in your area. Notify ERCOT of any abnormal line operations in your area.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Once RTCA and State Estimator are operational: Make a Hotline call to the ERCOT Transmission Operators: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator are now functioning and we are now back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 4 | If VSAT has not solved within 1.5 hours: - Manually run VSAT - If no results, contact Operations Planning Support - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. - If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |

# 2.1.3	OOME – VDI Guidelines

Procedure Purpose: To provide guidelines for OOMEs and VDIs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 |  |  |  |
|  | R4.2 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 1 does not apply to wind units. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOME’d off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, coordinate with the Frequency Operator for issuance of VDI to relieve the QSE from their Ancillary obligation if necessary. - Issue an instruction to release the QSE from the dispatch instruction so they can come back into compliance. |
| 5 | When an SPS activates and that SPS activation de-rates a resource or takes a resource off line, issue a VDI to the affected QSE. - The beginning time on the VDI will be the interval that the SPS activated. - The ending time on the VDI will be the interval the SPS was restored to service. - The exception will be VDI’s will not exceed four (4) hours after the time of activation. - If the resource is a DC tie, include the name and zone of the tie. Typical Script on the VDI: “SPS activation, caused <unit name or DC tie name> to <trip or runback>”. |
| 6 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with a Settlements only VDI stating “OOMC for Quick-start” on the VDI form. |
| 7 | As time permits, forward the VDI to the Shift Supervisor |

# 2.1.4	Three Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been place throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |

# 2.1.5	Monitoring Priority Outages in Real Time Monitor Mode

Procedure Purpose: To monitor priority outages in real time.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R1.9 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | A priority outage is one that affects generation. |
| 1 | Select the required outage or outages in the Outage Scheduler to be monitored in the Real-Time Monitor. |
| 2 | Select the “Toggle Monitor Flag” from the drop down and Apply. |
| 3 | Select switch to the Real-Time Monitor to view the monitored outage or outages. |
| 4 | Verify that the outage is being monitored by change in color to pink. |
| 5 | Monitor outages as required. |
| 6 | When a priority outage returns to service ensure the generation that was being dispatched is released when appropriate. |
| 7 | Notify the Shift Supervisor and make log entry as time permits. |

# 2.1.6	Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-003-2 R2 | IRO-005-1 R1.1, R1.2 | TOP-002-2 R8 |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: Page 1: 345 KV Transmission Equipment Status Page 2: 138 KV Transmission Equipment Status Page 3: Generator Breaker, AVR, and SPS Status Page 4: Transmission Line Overloads and Voltage Violations- critical alarms Page 5: AGC Status Page 6: RTNET Status Page 7: ICCP Status Page 8: EMS Task Application Status |
| 1 | Monitor the Alarm Summary Display pages 1, 2, 3, 4, and 8 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Frequency Control Desk to clear the alarms approximately every 2 to 3 hours or as needed. |

# 2.2.1	Real Time Contingency Analysis (RTCA)

Procedure Purpose: To monitor SOLs and have situation awareness of the transmission system

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1 & R4.2 | IRO-003-2 R1 | IRO-005-1 R1.2, R1.7, R3 | IRO-006-3 R1 |
|  | TOP-001-1 R1, R2 & R5 | TOP-002-2 R6, R8, R10 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit violations. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. |
| NOTE: | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Energy Management System (EMS) and an electronic copy is located on the ERCOT website under ‘Grid Information’ in the Transmission section. http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA) in the key document section. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 20 minutes. |
| 3 | If RTCA has not run within 20 minutes, refer to Section 2.1.3, Analysis Tool Outages. |
| 4 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist: - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are usually located in the daily Outage Notes. |
| 5 | If RTCA has run within 20 minutes, EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or -4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take appropriate voltage control action. |
| 6 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 7 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Desk Top Guide Section 3.6 for guidance. |
| 8 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 9 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 10 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 11 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Proceed to section 2.2.3 Potential IROL’s. |
| 12 | If congestion management techniques fail to resolve congestion and no practicable resource solution exists, ISSUE a Watch per section 2.5.3. |
| 13 | Periodically check the Base Case violations display for Thermal overloads. A “thermal overload in real-time” means loading above 100 % of the NORM/Continuous rating. |
| 14 | If a valid Thermal overload exists in real-time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 15 | Periodically check the “Contingency Solution Results” display. If there are unsolved contingencies, run the State Estimator again. If unsolved contingencies remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. If there are known reasons that the contingency is unsolved, as time permits, notify the on-call Operations Support Engineer to verify system conditions have not changed.. |

# 2.2.3 	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R3.2 & R4.2 | IRO-003-2 R1 | IRO-005-1 R1.2, R1.7, R3 | TOP-002-2 R10 |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, and if a SPS, RAP, PCAP, TOAP, or MP does not exists; this is considered to be a potential IROL. Corrective action must be taken within 30 minutes to reduce the flow below 125%. |
| 1 | If congestion management techniques fail to reduce the flow below 125% within 30 minutes and no practicable resource solution exists, take real-time snap shot and save it. Send an e-mail with the saved file name so analysis can be done at a later time to: - OPS Support Engineering - 1 ERCOT Shift Supervisors |
| 2 | Notify the Shift Engineer or the on-call Operations Support Engineer, ask for a Mitigation Plan. |
| 3 | Make log entry. |

# 2.2.4 	OOME when OC3 is not Effective

Procedure Purpose: A process to relieve congestion when an OC3 is not effective.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R2 | IRO-005-1 R1.7, R3 | IRO-006-3 R1 |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | All wind units have the non-bid flag checked in the Resource Plan which will prevent them from receiving local congestion instructions. When OC3 activation is not effective due to excessive wind generation output, the following steps shall be taken to OOME wind generation to relieve transmission congestion. |
| 1 | Activate an OC3 for local congestion as mentioned in Section 2.2.1. |
| 2 | Upon activation of the OC3, perform a Contingency Analysis study as indicated in Section 3.1 of the Desk Top Guide. |
| 3 | After performing a Contingency Analysis study, navigate to the Network Constraints Summary by going to Analyst Displays  Contingency Analysis Displays  Shift Factors, or typing NETSENS_CONSTRAINTS in the command line at the top of the display. |
| 4 | On the Network Constraints Summary Display, scroll to the constraint for which the corresponding OC3 was created. Click on the circle with an “i” inside it on the right hand side of the display. This will bring up the Network Constraints Details. |
| 5 | The Network Constraints Details display shows all units which have positive or negative shift factors above 1 % for the given constraint. Scroll through this list to find the wind units with the greatest positive shift factors. Note that this does not apply to the McCamey Area units, see procedure 2.2.14 when OOMing those units. |
| 6 | If local techniques fail to maintain system security, an Emergency Notice must be declared before Zonal Techniques may be utilized. |

# 2.2.7 	West - North Dynamic Stability Limit

Procedure Purpose: To maintain West to North stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R2 & R4.2 | IRO-003-2 R1 | IRO-005-1 R1.2, R1.7 & R3 | IRO-006-3 R1 |
|  | TOP-002-2 R10 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | If the current hour West-North Stability limit calculated on the W-N Stability spreadsheet changes in value or color, update the RTMONI limit on the “Stability-WN” monitor to the value shown on the spreadsheet. |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability.xls” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 3 | If the next hour Stability limit is significantly lower and reliability concerns exist that the stability limit may exceed the limit for more than 30 minutes, activating the OC1 may need to be implemented before 85% . |
| 4 | If the monitored flow on the Stability-WN monitor is approaching 85% and wind is climbing: - Activate the West – North OC1 - Change the W-N CSC limit to the Stability limit in RTMONI to give transparency to the Market. - Post a message on the MIS: Typical Script: “ERCOT is controlling the West - North Dynamic Stability Limit with the West – North OC1”. |
| 5 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - OOME/VDI wind down - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control the West to North dynamic stability limit.” |
| NOTE: | If Zonal Techniques failed to control the West-North Stability limit and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |

# 2.2.11	SPS Monitoring

Procedure Purpose: To monitor and prevent an SPS operation if possible.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R4.2 | IRO-005-1 R1.1 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | If notified to take a SPS in/out of service, ensure OPS Planning is notified. |
| NOTE: | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE: | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingent loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario congestion management is not needed until the criterion in Desk Top Guide Section 3.3 is met. |
| 1 | Special Protection Schemes (SPS) - EXAMINE the results in RTCA for SPS activation. - If “SPS” is identified as a post contingent overload, EXAMINE the color of the background. - Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\system operations\Remedial Action Plans> |
| NOTE: | Typically SPS’s are to solve post-contingent overloads on the Transmission System. Due to outages, either (Planned or Forced) the Transmission topology is changed temporarily. During these conditions the ERCOT Transmission & Security operator(s) will utilize Congestion Management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | Monitor the Excel spreadsheet “Real Time Values” - Each SPS will be displayed, as the SPS activation threshold increases the display changes colors - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 3 | If the system operator receives a call from a TSP or as the threshold increases on the SPS to greater than 90%, then congestion management techniques should be employed in an attempt to prevent its’ activation. |
| NOTE: | If notified by a QSE that an SPS operates (runback or trip) refer to procedure: - 2.1.4 OOME – VDI Guidelines |

# 2.4.4 	Power System Stabilizers (PSS) and Automatic Voltage Regulators (AVR)

Procedure Purpose: To ensure that power system stabilizers and automatic voltage regulators stay “in service” whenever possible.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R1.1 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT Protocol Section 6.5.7.2, QSE Responsibilities states that “…any QSE-controlled power system stabilizers will be kept in service unless specifically permitted to operate otherwise by ERCOT…” Operating Guide Section 2.2.4, Automatic Voltage regulators and Power System Stabilizers also states that PSSs must be in service whenever possible. The Transmission Operator shall know the status of all transmission Reactive Power Resources, including the status of voltage regulators and power system stabilizers (PSS). (VAR-001-1) (R6) Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes …a status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. (VAR-002-1) (R3.1) |
| NOTE: | QSE’s will inform ERCOT of a change in status with any PSS or AVR by phone. |
| 1 | The ERCOT Operator will: - Ensure that the QSE has notified the TO of the change in status. - Enter the status change information into the ERCOT Logs - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being taken in or out of service). - Cut and paste the log entry into an e-mail and send to - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability.xls” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| NOTE: | Operations Planning will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at: \\cpwp004d\departments\Operations Support\Operations Planning\AVR and PSS Status |

# 2.5.3	Issue a Watch

Procedure Purpose: To inform the Market Participants of a Watch.

| Protocol Ref. | 5.6.5 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.3 |  |  |  |
| NERC Std. | COM-002-2 R2 | EOP-001-0 R4.1 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits with no practicable resource solution - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition - There is a hurricane in the Gulf with expected landfall in Texas - A cold front has arrived with temperature anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - Forced Outages or other abnormal operating conditions occur with no practicable resource solution - Adjusted Responsive Reserve drops below 2500 MW - A transmission condition has been identified that requires emergency energy from any of the South DC-Ties. |
| 2 | Issuance of a Watch requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Before issuing a Transmission Watch for transmission issues, notify the TO and discuss the actions you are about to take. |
| 4 | When issuing a Watch for a transmission issue, use the following script for making the hotline call: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission Watch due to the [planned or forced] outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” Note: If the facility outage is a generator state “a generating unit”. |
| 5 | Typical MIS and ENS posting script: ERCOT issued a Transmission Watch due to the [planned or forced] outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” |
| 6 | When issuing a Watch for other reasons, use the following script for posting the message and making the hotline call: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

# 2.5.4	Issue an Emergency Notice

Procedure Purpose: To inform the Market Participants of an Emergency Notice.

| Protocol Ref. | 5.6.6 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.4 |  |  |  |
| NERC Std. | COM-002-2 R2 | EOP-001-0 R2 & R4.1 |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notification Messaging System. |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no practicable resource solution exists. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability |
| 2 | Issuance of an Emergency Notice requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Before issuing an Emergency Notice for transmission issues, notify the TO and discuss the actions you are about to take. |
| 4 | When issuing an Emergency Notice for a transmission issue, use the following script for making the hotline call: Typical Script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice due to the [planned or forced] outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” Note: If the facility outage is a generator state “a generating unit”. |
| 5 | MIS and ENS posting script: ERCOT issued an Emergency Notice due to the [planned or forced] outage of (facility that is actually out). The loss of (name of contingency) overloads (name of overloaded element).” |
| 6 | When issuing an Emergency Notice for other reasons, use the following script for posting the message and making the hotline call: Using the Hotline, notify all TOs of the Emergency Notice. - When TOs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.6	 Monthly Testing of Satellite Phone System

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R2 |  |  |  |

| Approved by: |  |  | Effective Date: June 18, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in Section 7 of the Desktop Guide for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Section 7 of the Desktop Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form. An electronic copy of this form is located in P:\ SYSTEM OPERATIONS”\Satellite Bridge Testing forms” folder. |
| 4 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the form is complete. |
| 5 | Log the test date and results in the ERCOT Operations Log. |
| 6 | When working out of the Back-up during the monthly scheduled dates, test at least one Satellite phone. If any problems are encountered, followed step 7. |
| 7 | Verify with the Shift Supervisor that the following personnel are notified for any Satellite phone problems during the test by e-mail: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |