## Power Operations Bulletin # 425

ERCOT has revised the Frequency Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

# 5.4	Monitor and Control Time Error Correction

Procedure Purpose: This procedure will establish the standard for implementing time error correction

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 2.2.7 |  |  |  |
| NERC Std. | BAL-004 |  |  |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT ISO is the Reliability Coordinator and Balancing Authority that implements and terminates ERCOT Time Corrections in accordance with ERCOT Protocols and Operating Guides. ERCOT Reliability Coordinator is the Interconnection Time Monitor within the ERCOT Interconnection. |
| REQUIREMENTS: | When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. Time error corrections normally start and end on the hour or half-hour. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction. However, at no time should the accumulated time error be allowed to exceed five (5) seconds. Time error correction notifications shall be labeled alphabetically on a monthly basis (A-Z). In the succeeding month, the first time error correction will revert back to “A”. |
| 1 | DISPLAY the Generation Area Status display. Reference Display: Generation Area Status – Time Error – “Correction Schedule” |
| 2 | Select Time Error – Correction Schedule. |
| 3 | ENTER the appropriate Time error ID letter. |
| 4 | ENTER the frequency offset using – 0.02 for fast time correction (59.98 Hz) or +0.02 for slow time correction (60.02 Hz). |
| 5 | ENTER a Start Time later than the current time AND ENTER a Stop Time later than the scheduled start time. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 6 | Notify all QSEs using a hotline call, if available, before starting time correction, of the start time and frequency offset. Typical script: “This is ERCOT operator [first and last name]. ERCOT is initiating a time error correction, we will ENTER the frequency offset using [– 0.02] or [+0.02] at [time]. The current time error is [time]. Thank you.” Print Hotline Log, ensure printout has date and time, and forward to Shift Supervisor. |
| 7 | VERIFY the Manual radio button to be selected. Time correction will start at selected date and time. Reference Display: Generation Area Status – “Time Error” – Correction Schedule |
| 8 | Monitor the time error on the Generation Area Status Display until it reaches an acceptable value (+/- 0.5 seconds). Time error correction may be terminated after five hours, or after any hour it has reached an acceptable value of +/- 0.5 seconds. |
| 9 | If a time error correction is prematurely terminated, wait at least one hour between sending the termination and re-initiation notices. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 10 | - Notify all QSEs using a hotline call, if available, before ending time correction. Typical script: “This is ERCOT operator [first and last name]. ERCOT is ending the time error correction at [time]. The current time error is [time]. Thank you.” - Print Hotline Log, ensure printout has date and time, and forward to Shift Supervisor. |
| 11 | LOG in the Operator’s Log start time, stop time, Time error ID letter, time error, and frequency offset for each start and termination. |

## 2.6.3	 Issue a Watch

Procedure Purpose: To inform the Market Participants of a system Watch

| Protocol Ref. | 5.6.5 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.3 |  |  |  |
| NERC Std. | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-1 R1.10 |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must issue a Watch before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services, or Emergency Short Supply Spinning Reserve Services. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits with no practicable resource solution - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - There is a hurricane in the Gulf with expected landfall in Texas - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A situation is emerging that will have an adverse effect on grid reliability - Loss of communications or control condition is pending or in progress. - Adjusted Responsive Reserve drops below 2500 MW |
| 2 | Issuance of a Watch requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Watch. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.4	 Issue an Emergency Notice

Procedure Purpose: To inform the Market Participants of an Emergency Notice.

| Protocol Ref. | 5.6.6 | 4.8 |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.4 |  |  |  |
| NERC Std. | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-1 R1.10 |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Knowledge of an emerging/existing situation that could/does require intervention to ensure system reliability requires ERCOT to notify Market Participants through the use of Emergency Notifications. |
| 1 | As directed by the Shift Supervisor, OR when appropriate, ISSUE an Emergency Notice IF: - A transmission condition has been identified causing unreliable operation or overloaded elements. - A short supply, congestion condition is affecting voltage and/or frequency with risk of grid area failure(s) and no practicable resource solution exists. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures. |
| 2 | Issuance of an Emergency Notice requires: - Posting on the ENS - Posting on the MIS - Notifying QSEs via the Hotline |
| 3 | Using the Hotline, notify all QSEs of the Emergency Notice. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for [state Emergency Notice]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.6.6	 Provide Advance Notice of Diminishing Responsive Reserve

Procedure Purpose: Guidelines for issuing advance notice of diminishing Responsive Reserves

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 R2.4 | EOP-001-0 R3.1 | EOP-002-2 R1, R2, R4 & R6.1, R6.2, R6.4, R8 | IRO-005-1 R1.4, R1.5, R4 |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS |
| 1 | Using the Hotline to issue the Advisory, notify QSEs when Adjusted Responsive Reserve is equal to or less than 3000 MW. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen below 3000 MW. Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |
| 3 | Instruct the Transmission & Security Desk Operator to notify the TOs that an Advisory has been issued. |
| 4 | Ensure the following is posted on the ENS and MIS: - Advisory issued for ARR below 3000 MW. |
| 5 | When adjusted Responsive Reserve falls below 2500 MW: Using the Hotline, notify QSEs: - When QSEs have answered the Hotline, print Hotline log. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch to provide notice that Adjusted Responsive Reserve has fallen below 2500 MW. - Please keep your Resource Plan updated and notify ERCOT of any changes that will prevent you from meeting your Responsive Reserve obligation. - ERCOT ISO is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. - Suspend all ERCOT required generation unit testing. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Ensure the Operating Period Operator has deployed Non-Spin for ARR below 2500 MW. |
| 7 | If additional generation is needed, OOME to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market and show “On” and “Plan MW” = 0. If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0. Follow up with a Settlements only VDI stating :OOMC for Quick-start” on the VDI form. |
| 8 | Instruct the Transmission & Security Desk Operator to notify the TOs that a Watch has been issued. |
| 9 | Ensure the following is posted on the ENS and MIS: - Watch issued for ARR below 2500 MW. |

## 2.6.10	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the Back-up Control Center (BCC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R5 | EOP-001-0 R4.4 | EOP-008-0 | IRO-005-1 R1.10 |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC (cell phone or Emergency Power Fail (EPF) phones), THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the BCC - Notify them of the situation AND - Have them attempt to make contact with Security at TCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT is declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT declaring an emergency and is transferring operations to the backup control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT if thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, West - North and North – Houston stability limits if power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Issue a VDI to the QSE that was put on constant frequency, as time permits. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support, Telecommunications - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.7.10	Loss of E-Tagging

Procedure Purpose: Contingency plan for loss of E-tagging capability

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 0 |  |

| Step | Action |
| --- | --- |
| 1 | If OATI goes down for an unknown reason (i.e. maintenance), contact the operator at the primary to check on their connectivity. If their system is also down, contact the OATI help desk to see if the issue is on their end. If issue is not on the OATI end, contact the ERCOT help desk. |
| 2 | Determine the estimated down time, if longer than 30 minutes, notify the SPP Reliability Coordinator and the DC-Tie Operators. |
| 3 | Post message on MIS: Typical Posting: “ERCOT ISO E-tagging is down; we are unable to accept new schedules across the DC-Ties at this time”. |
| 4 | No new E-tags with be accepted, only curtailments required by SPP: - Coordinate with SPP and the appropriate DC-Tie Operator - Notify Operating Period desk to adjust off-set |
| NOTE: | Before-the-fact and after-the-fact check outs will not be available |
| 5 | Once OATI is available, confirm SPP and the DC-Tie Operators availability. If available for all parties: - Update the MIS posting to “invalid” If curtailments were made while OATI was down, ensure E-tags are updated |

## 2.7.11	Emergency Energy across the CFE DC Ties

Procedure Purpose: Steps to secure emergency energy across the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R3.1, R7.2 & R7.3 | EOP-002-2 R1, R2 & R4 & R6.1, R6.2, R6.4 & R8 | INT-010-1 R3 | IRO-005-1 R4 |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must declare a Watch or an emergency and make the proper posting/hotline call when receiving emergency energy from CFE, whether it is for transmission issues or an EEA situation. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| NOTE: | If there are E-tags that can be curtailed to alleviate the emergency situation, referred to Procedure 2.7.6, Step 5. When notified by Hotline If in EEA situation, export E-tags should be curtailed first before emergency energy is received. |
|  | When notified by Hotline that ERCOT has implemented an EEA level, proceed with this procedure |
| 1 | When ERCOT is in need of the Emergency Energy: When notified by the Transmission & Security Desk of the need for emergency energy for a transmission issue or if in an EEA situation: - If there is import capacity room on the appropriate DC-Tie(s), contact AEP Corpus and request that they contact CFE to see if emergency energy is available - If emergency energy is available, determine the DC-Tie(s), MW amount, time and duration (if possible), - Request AEP Corpus to ramp the appropriate DC-Tie with the emergency energy - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Forward VDI(s) to Shift Supervisor (fax) as time permits |
| 2 | When CFE is in need of the Emergency Energy: The request will come from either the Transmission & Security Desk or AEP Corpus: - If there is export capacity room on the appropriate DC-Tie(s), coordinated with the Transmission & Security Desk to ensure it will not cause ERCOT transmission issues - With no issues, determine the DC-Tie(s), MW amount, time and duration (if possible) - Coordinate with Operating Period Desk - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Notify AEP Corpus to ramp DC-Tie(s) - Forward VDI(s) to Shift Supervisor (fax) as time permits |

## 2.7.12	EEA 1 Schedule across the SPP DC Ties for EEA 1

Procedure Purpose: Steps to secure a schedule across the SPP DC tie(s) in an Energy Emergency Alert 1.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R3.1, R7.2 & 7.3 | EOP-002-2 R1, R2 & R4, R6.1, R6.2, R6.4 & R8 | INT-010-1 R3 | IRO-005-1 R4 |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Once notified by Hotline, the DC-Tie Operator at the back-up is responsible for carrying out this procedure. |
| 1 | Notify the SPP Reliability Coordinator of ERCOT’s EEA 1 status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. We will contact the Tariff desk to inquire about the availability of transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2A, 2B, or 3, proceed to Section 2.7.12 If there is transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the transmission service available. Thank you.” |
| NOTE: | SPP will contact PSEs with unscheduled reservations and notify them of ERCOT’s EEA 1 status. PSEs may choose to use their reservation to schedule into ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers): Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-Tag(s) and proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify the DC Tie Operator of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag (s) for an EEA 1 schedule. |

## 2.7.13	Emergency Energy across the SPP DC Ties for EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the SPP DC tie(s) in an Energy Emergency Alert 2A, 2B or 3.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R 3.1, R7.2 & R7.3 | EOP-002-2 R1, R2, R4, R6.1, R6.2, R6.4, & R8 | INT-010-1 R3 | IRO-005-1 R4 |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE: | If ERCOT goes directly to an EEA 2A, 2B or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below. |
| 1 | Notify the SPP Reliability Coordinator or ERCOT’s EEA status Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will contact the Tariff desk to inquire about the availability of emergency transmission service, please transfer me.” |
| 2 | Notify the SPP Tariff desk to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continue with script: “I will be contacting AEP QSE to inquire about the availability of capacity not to exceed the emergency transmission service available. Thank you.” |
| NOTE: | ERCOT must have the Reliability Coordinator Information System (RCIS) updated with the EEA 2 or 3 status before SPP grants emergency transmission service. |
| NOTE: | SPP will curtail all non-firm transmission service schedules going out of ERCOT. |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to submit the transmission request and if approved submit the E-Tag(s). Proceed to step 4. Issue a VDI to QSE. |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status: Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| NOTE: | Keep SPP informed of ERCOT’s status. |

## 2.7.14	Backing out of EEAs and Termination

Procedure Purpose: Steps to back out off and terminate schedules and/or emergency energy across the SPP DC ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 |  |  |  |
|  | R1 |  |  |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | When moving EEA status: Notify the SPP Reliability Coordinator of ERCOT’s status. Typical script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify the Tariff desk, please transfer me. Thank you.” |
| 2 | Notify the SPP Tariff desk of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We will notify AEP. Thank you.” |
| 3 | Notify AEP QSE (AEP Generation Dispatchers). Transmission Service is only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| 4 | Notify AEP DC-Tie Operator of ERCOT’s EEA status. Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| NOTE: | Repeat above steps with the notifications until ERCOT’s status is EEA 0 (zero). |

## 2.7.15	Fast Start Emergency Energy to SPP

Procedure Purpose: Steps to provide emergency assistance to Southwest Power Pool across the SPP DC ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R7.2 & R7.3 |  |  |  |

| Approved by: |  |  | Effective Date: July 15, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Every effort should be made to render assistance during emergency conditions. SPP will notify ERCOT that emergency assistance is needed. |
| 1 | VERIFY that providing emergency assistance to SPP will not put ERCOT in an insecure state, or worsen an existing insecure state. |
| NOTE: | SPP will contact the DC Tie Operator and arrange to maximize the DC tie output into SPP. It is not necessary to confirm that an emergency condition has been posted in the Reliability Coordinator Information System (RCIS). SPP may need to act before the RCIS is updated. |
| 2 | Notify the Operating Period Desk to adjust the Offset to minimize the use of Regulation. |
| 3 | When possible: - Contact AEP QSE and instruct them to create and submit an E-Tag for the emergency assistance (this can be done after-the-fact but within an hour of the event). - Issue a VDI to AEP QSE for the emergency assistance. |