Power Operations Bulletin # 429

ERCOT has revised the Operating Period Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1.2	Respond to Hour-Ahead Study Results

Procedure Purpose:  To determine A/S scheduling shortage in Hour-Ahead

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002-2 R1 |  |  |  |

| Approved by: |  |  | Effective Date: August 03, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 3.0 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| 1 | REVIEW HA details of the study. |
| 2 | VERIFY URS margin is acceptable (not indicated in red or due to rounding errors) and proceed. IF in red: - Select interval with largest deficiency, right click and select “show output for this interval”  Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved. - If deficiency still exists, operators may contact the QSE to request an updated Resource plan. |
| 3 | VERIFY DRS margin is acceptable (not indicated in red or due to rounding errors) and proceed. IF in red: - Select interval with largest deficiency, right click and select “show output for this interval” - Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved. - If deficiency still exists, operators may contact the QSE to request an updated Resource plan. |
| 4 | VERIFY RRS margin is acceptable (not indicated in red or due to rounding errors) and proceed. IF in red: - Select interval with largest deficiency, right click and select “show output for this interval”  Identify the QSE where deficiency exists, and wait until the Real Time Balancing Market has solved - If deficiency still exists, operators may contact the QSE to request an updated Resource Plan. |
| 5 | - Identifying NSRS margin is not possible using the MOI with the implementation of PRR776. - For NSRS calculations, Resources must also be available, off line and have NSRS checked in the resource plan to be counted in the Excel MAI. |
| NOTE: | If the QSE agrees to correct the deficiency, log and take no further immediate action. If they are unable to correct the deficiency (i.e. Insufficient resources are available to provide agreed upon services), then notify the Shift Supervisor of possible protocol violation(s). |
| NOTE: | Once the maximum procurement level has been reached, increasing the offset will not lead to additional balancing deployment. The maximum procurement level is reached once “Net Gen” and “Net Load” no longer matches in the Real-Time Balancing Market window. Should Balancing Energy become depleted, over compensating with excessive offsets can potentially cause unexpected deployments when more balancing becomes available. |
| NOTE: | Deployment of NSRS is based on the Excel MAI along with a reasonable load forecast. Recall is based on real-time UBES bid availability or other reliability conditions. |

| 6 | Using the Excel MAI, verify UBES bids remaining. - If >20% of available UBES bids remain undeployed, no further action is necessary. - If <20% of available UBES bids remain undeployed, verify that UBES is available in real-time before entering the offset. - If >5% of available UBES bids remain undeployed, no further action is necessary. - If <5% remaining proceed. |
| --- | --- |
| 7 | DETERMINE if NSRS deployment is necessary for balancing support or shortage of adjusted Responsive Reserve. IF NSRS is scheduled and available, deploy for a minimum of one hour and continue as needed. If NSRS is necessary, scheduled and available, communicate with the Shift Supervisor to ensure an active constraint won’t be negatively impacted, then deploy NSRS as scheduled and needed to resolve UBES bid deficiency. |
| 8 | When NSRS is deployed, notification is automatically made to the Market Participants at the following link: http://mospublic.ercot.com/ercot/jsp/balancing_services_mcp.jsp |
| 9 | When UBES bids remaining exceeds the amount of NSRS deployed by 10% or greater. Communicate with the Shift Supervisor and allow NSRS to end. |