## Power Operations Bulletin # 432

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.1.2	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: August 4, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | If RTCA or the State Estimator has not solved within the last 10 minutes, refer to Desk Top Guide Section 3.1 and run through the checklist. If, after trying all the checks and RTCA and/or the State Estimator still has not solved, notify the on-call State Estimator Support Engineer and request the tool(s) be restored to operation as soon as possible. If RTCA will not solve but the EMS is available notify the on-call Operations Engineer to request limits be calculated manually. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 30 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to the ERCOT Transmission Operators: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 30 minutes. Please monitor your own service area and notify ERCOT if thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits if power flows reach 85% of their respective limits. Continue to monitor voltages in your area. Notify ERCOT of any abnormal line operations in your area.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Once RTCA and State Estimator are operational: Make a Hotline call to the ERCOT Transmission Operators: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator are now functioning and we are now back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 4 | If VSAT has not solved within 1.5 hours: - Manually run VSAT - If no results, contact Operations Planning Support - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. - If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |

# 2.1.3	OOME – VDI Guidelines

Procedure Purpose: To provide guidelines for OOMEs and VDIs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 |  |  |  |
|  | R4.2 |  |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 1 does not apply to wind units. |
| 1 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 2 | When system conditions require one CT of a Combined Cycle Plant to be OOME’d off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 3 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 4 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, coordinate with the Frequency Operator for issuance of VDI to relieve the QSE from their Ancillary obligation if necessary. - Issue an instruction to release the QSE from the dispatch instruction so they can come back into compliance. |
| 5 | When an SPS activates and that SPS activation de-rates a resource or takes a resource off line, issue a VDI to the affected QSE. - The beginning time on the VDI will be the interval that the SPS activated. - The ending time on the VDI will be the interval the SPS was restored to service. - The exception will be VDI’s will not exceed four (4) hours after the time of activation. - If the resource is a DC tie, include the name and zone of the tie. Typical Script on the VDI: “SPS activation, caused <unit name or DC tie name> to <trip or runback>”. |
| 6 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with a Settlements only VDI stating “OOME for Quick-start” on the VDI form. |
| 7 | As time permits, forward the VDI to the Shift Supervisor |

# 2.2.1	Real Time Contingency Analysis (RTCA)

Procedure Purpose: To monitor SOLs and have situation awareness of the transmission system

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1 & R4.2 | IRO-003-2 R1 | IRO-005-1 R1.2, R1.7, R3 | IRO-006-3 R1 |
|  | TOP-001-1 R1, R2 & R5 | TOP-002-2 R6, R8, R10 |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit violations. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. |
| NOTE: | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Energy Management System (EMS) and an electronic copy is located on the ERCOT website under ‘Grid Information’ in the Transmission section. http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA) in the key document section. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 10 minutes. |
| 3 | If RTCA has not run within 10 minutes, refer to Section 2.1.2, Analysis Tool Outages. |
| 4 | EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist: - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\departments\System Operations\Remedial Action Plans> A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are usually located in the daily Outage Notes. |
| 5 | EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage violations greater that the emergency switchyard voltage rating exists at the STP and CPSES 345 kV buses. For Comanche Peak System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or -4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. For South Texas Project System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +2% or -4%. Maximum Voltage; 369.5 kV. Minimum Voltage; 347.8 kV. If post-contingency violations greater than the Emergency Rating exist, COORDINATE with the Transmission Operator and QSE and take appropriate voltage control action. |
| 6 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 7 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Desk Top Guide Section 3.6 for guidance. |
| 8 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 9 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 10 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 11 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Proceed to section 2.2.3 Potential IROL’s. |
| 12 | If congestion management techniques fail to resolve congestion and no practicable resource solution exists, ISSUE a Watch per section 2.5.3. |
| 13 | Periodically check the Base Case violations display for Thermal overloads. A “thermal overload in real-time” means loading above 100 % of the NORM/Continuous rating. |
| 14 | If a valid Thermal overload exists in real-time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 15 | Periodically check the “Contingency Solution Results” display. If there are unsolved contingencies, run the State Estimator again. If unsolved contingencies remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. If there are known reasons that the contingency is unsolved, as time permits, notify the on-call Operations Support Engineer to verify system conditions have not changed.. |

# 2.2.2 	Real Time Constraint Activity Manager (RTCAM)

Procedure Purpose: To alleviate congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R4.2 | IRO-005-1 R1.2, R1.7 & R3 | IRO-006-3 R1 |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | Local Congestion Management Techniques consist of OC3s, Unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| NOTE: | Phase shifters could at times be used to help with congesting management: - Putnam – NW/WN transfers to increase CSC transfer capability - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |
| Note: | To determine the Laredo Import utilize the RTCA results. In the event that RTCA is unavailable and RTMONI is available utilize the Laredo Import display to determine the import. Outages in the area may affect this and Operations Support will determine the import limit in those instances. |
| 1 | VERIFY SFT is enabled in the MOI. - This can be determined by making sure that the check box next to “Run SFT for Real-Time Markets” on the Real-Time Balancing Market display is checked. If it is not checked, then check it. |
| 2 | DETERMINE if RTNET and RTCA has solved within 10 minutes. |
| 3 | If RTNET and/or RTCA have not solved within 10 minutes, refer to Section 2.1.3, Analysis Tool Outages. |
| 4 | DETERMINE if RTNET has solved with a solution status of “VALID SOLUTION – NO SFT CASE.” - If RTNET has this solution, notify the State Estimator On-Call Engineer. |
| 5 | EXAMINE the RTCAM Branch Violations and Operating Constraints List. |
| 6 | EXAMINE the constraints with the “Active” check box filled in. - VERIFY that an OC3 is created for all overloaded active constraints in the MOI by selecting the “constraint” tab from the “Real-Time Balancing Market” screen in the MOI. In the Type column, sort descending. All OC3s will be sorted to the top of the page. - If an overloaded constraint is active in RTCAM, but the corresponding OC3 is missing from the MOI, LOWER the value in the “% Rating” column in RTCAM to tighten the constraint until the OC3 appears in the MOI. - If an OC3 is active in the MOI, but the corresponding constraint in RTCAM is well below the monitored rating, INCREASE the value in the “% Rating” column in RTCAM to loosen the constraint. |
| 7 | When an OC3 deploys quick start units for congestion, do one of the following: - Issue an “OOME VDI” for settlements on the quick start unit(s) that are required to mitigate congestion - Issue an OOME for quick start unit(s) using the OOM tool and keep the OC3 active, or - Use OOM tool to OOME for quick start unit(s) instead of activating an OC3, or - Issue a VDI to disregard the unit specific deployment and write “instructed deviation” on the VDI if congestion can be resolved without unit(s) OOME VDI for quick start units will only be given under the local congestion scenario, balancing and zonal deployments are not included. Follow up with a Settlements only VDI stating “OOME for Quick-start” on the VDI form. |
| 8 | To activate a constraint, check the “Active” check box next to the constraint to be activated. The text in this row of data will change to red and it will be immediately sorted to the top of the display. |
| 9 | To deactivate a constraint, uncheck the “Active” check box next to the constraint. Uncheck the “Retain” check box as well, if desired. Leaving the “Retain” box checked will only cause the constraint to remain on the Operating Constraints List display when an overload is not occurring. |
| 10 | To acknowledge constraints that are determined to be erroneous or are already accounted for, check the check box in the “Ack.” Column. This will sort the constraint to the bottom of the display. |
| 11 | Special Protection Schemes (SPS), Remedial Action Plans (RAP), and Pre-Contingency Action Plan (PCAP) analysis - EXAMINE the results in RTCAM for RAP or SPS activation, using the “SPS” and “RAP” columns on the Operating Constraints List display. - If “SPS” and/or “RAP” is checked, EXAMINE the color of the background. Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. - ADJUST initial “% Rating” higher if activating a constraint for a post-RAP/SPS overload if needed. This is because RTCAM/SFT can not model RAP/SPS when generating OC3 constraints so they tend to over-constrain at 100 % of rating. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\departments\System Operations\Remedial Action Plans> |

# 2.2.5  	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: Processes to relieve local congestion surrounding the CFE DC-Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R3.2 & R4.2 | IRO-005-1 R1.7 & R3 | IRO-006-3 R1 |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. |
| NOTE: | ERCOT may adjust generation to solve local congestion in the areas of the CFE DC-Ties; however OOMC’s will not be utilized to allow schedules to flow. |
| NOTE: | When curtailing E-tags for transmission issues, they should only be curtailed for a couple hours at a time, hourly if possible. |
| NOTE: | In the event that RTCA is unavailable and RTMONI is available utilize the Laredo Import display to determine if a E-Tag must be curtailed. |
| 1 | Update RTMONI with the CFE DC-Tie Limits each night across midnight. |
| 2 | If E-Tags must be curtailed to control post-contingency overloads: - Contact the ERCOT DC-Tie Operator to have the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 3 | If E-Tags must be curtailed to control the Valley or Laredo Import: - Contact the ERCOT DC-Tie Operator once the Valley Import is at 90% or a contingency related to the Laredo Import is in RTCA and expected to continue to climb. - Instruct the appropriate DC-Tie E-Tag curtailed to needed MW level, allowing at least 20 – 30 minute notice for curtailment - Notify the Shift Supervisor |
| 4 | If curtailments are being made, keep RTMONI updated with new limits. |
| 5 | As room becomes available, keep the ERCOT DC-Tie Operator notified so E-tags can be re-loaded |
| 6 | ERCOT must declare a Transmission Watch or Emergency in order to curtail E-Tags immediately. If a Watch or Emergency has been declared for a transmission issue: - Contact ERCOT DC-Tie Operator to have the appropriate DC-Tie ramped to needed MW level - Ensure the Transmission Watch or Emergency has been posted on the ENS and MIS - Notify the Shift Supervisor |
| 7 | ERCOT will curtail E-Tags for CFE for their transmission issues or emergencies. If contacted by AEP Corpus of a CFE issue: - Identify if at least 20 – 30 minute notice can be given for curtailment - Notify ERCOT DC-Tie Operator with information to make curtailment - Notify the Shift Supervisor |

# 2.2.8 	North-Houston Voltage Stability Limit

Procedure Purpose: To maintain North to Houston voltage stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R2 & R4.2 | IRO-003-2 R1 | IRO-005-1 R1.2, R1.7, R3 | IRO-006-3 R1 |
|  | TOP-002-2 R10 |  |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| VSAT | Initiate a manual Run Sequence for the Network Online Sequence after the change in the system typology. This process will give new VSAT results after RTNET, RTCA and RTDCP (VSA) is completed. |
| 1 | VSAT should be checked at least every hour, or more frequently as necessary. If North-Houston 345kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. |
| 2 | Determine if the Reliability margin is 500 MW of the Reliability margin: - O-HOUS_L ≤ 500 MW - N-H G ≤ 500 MW - N-H L ≤ 500 MW If the value is within 500 MW of the Reliability margin: - Request TSP’s in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| 3 | Determine if the Reliability margin is 300 MW of the Reliability margin: - O-HOUS_L ≤ 300 MW - N-H G ≤ 300 MW - N-H L ≤ 300 MW If the limit value is at the 300 MW Reliability margin: - Activate the North – Houston OC1 - Change the North – Houston CSC limit in RTMONI to the N-H VSAT Transfer Limit located in VSAT for Market transparency. - Post a message on the MIS: Typical Script: “ERCOT is controlling the North - Houston dynamic stability limit with the North – Houston OC1”. |
| 4 | Determine if the Reliability margin is 200 MW of the Reliability margin: - O-HOUS_L ≤ 200 MW - N-H G ≤ 200 MW - N-H L ≤ 200 MW If the limit value is at 200 MW Reliability margin: - Fleet up in Houston area generation - Deploy Non-Spin in the Houston zone and utilize quick starts not bid in as Non-Spin - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control North – Houston dynamic stability limit.” |
| 5 | Determine if the Reliability margin is 100 MW of the Reliability margin: - O-HOUS_L ≤ 100 MW - N-H G ≤ 100 MW - N-H L ≤ 100 MW If the limit value is at 100 MW Reliability margin: - Make Hotline call to deploy LaaRs in the Houston zone that are bid into the Responsive Reserve market. Typical Script: This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is instructing QSE’s to deploy LaaRs located in the Houston Zone that are bid into the market within ten (10) minutes. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Determine if the Reliability margin is 0 MW of the Reliability margin: - O-HOUS_L ≤ 0 MW - N-H G ≤ 0 MW - N-H L ≤ 0 MW If the limit value is at 0 margin for 15 minutes or greater: - Instruct Centerpoint to drop firm load in 100 MW blocks. Typical Script: This is ERCOT operator [first and last name]. ERCOT is instructing Centerpoint to drop [*** MWs] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete and give the amount of load shed. Please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |

# 2.2.10 	Pre-Contingency Action Plans

Procedure Purpose: To implement a Pre-Contingency Action Plan.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R1.2, R1.7 | IRO-006-3 R1 |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| CAUTION: | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability. |
| 1 | When RTCA shows a post-contingency overload and a PCAP exists to resolve it, - REVIEW the PCAP with the associated Transmission Operator. - Notify the Shift Supervisor of the anticipated actions. |
| 2 | Direct the execution of the PCAP with the associated transmission operator: Typical script: “This is ERCOT operator [first and last name]. ERCOT is instructing [TO] to implement the **** PCAP and [open/close] [breaker(s)]. [TO] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 4 | Between 0000 and 0500 each day, the Transmission & Security Desk Operator should review the logs and verify that no PCAP remain in effect from the preceding day. IF any PCAPs are still in use, evaluate system conditions to determine if: - The PCAPs should remain in effect, OR - The system should be returned to a normal status. |
| 5 | IF the ERCOT System Operator and Shift Supervisor agree that the PCAP is no longer needed, the Transmission & Security Desk Operator shall direct the TO to: - Return the system to its’ normal status, OR - Return the system to its’ status prior to implementation of the PCAP Which ever state is applicable. |

# 2.2.14 	Managing Generation Resources in McCamey Area

Procedure Purpose: To maintain stability of the wind powered generation in the McCamey area.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Rapid Response Wind Farms (RRWF) are designated as such under the Wind Unit Limitations located at the following link. All other units on the list are Slow Response Wind Farms (SRWF): https://tcr.ercot.com/default.cfm?func=tcrpostings |
| NOTE: | In real time operations, “Total Transmission Capacity” and “Maximum output allowed by system conditions” refers to RTCA or RTNET study results. Slow Response Wind Farms can respond to ERCOT Dispatch Instructions no more often than one instruction per three consecutive hours. The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. McCamey area wind generation will use VDIs to set initial wind limits prior to the operating day. |
| 1 | Use the wind limits from the “Transmission Limits to be Monitored” sheet developed by the Operations Engineers on the VDIs. |
| 2 | RRWF are allowed to operate above their daily limits. If operating above their limits is causing system problems, then call the RRWF and instruct them to come back to their daily limit |
| 3 | If the Total Transmission Capacity in the McCamey area is less than the total amount of “Wind Unit Limits” allocated to both SRWF and RRWF, THEN: 3.1 Instruct the RRWFs to reduce output such that the congestion is relieved. This instruction should be for a minimum of one (1) hour duration (constitutes 4 consecutive 15-minute intervals). - 3.2 On the fifth interval, instruct each SRWF to reduce its output by 10 Mw for a minimum of three hours. - 3.3 After each SRWF has reduced its output by 10 MW, and system conditions permit, the RRWF dispatch instruction can be released. |
| 4 | At least three hours after performing Step 3.2 above, and if system conditions permit, perform step 4.1, otherwise perform 4.2 4.1 Resume operation of the SRWFs up to an output level that will allow RRWF to operate at or above their “Wind Unit Limits” ownership levels. OR 4.2 Dispatch both SRWF and RRWF to levels that will allow them both to operate to the maximum allowed based on capacity-ratio-share. (Refer to the calculation tab on the Real-Time Values spreadsheet to calculate the capacity-ratio-share) |

# 2.4.1 	Respond to Voltage Issues

Procedure Purpose: Maintain acceptable voltage levels on the electrical grid.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-1 R1.2 & R1.4 | TOP-002-2 R8 |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | In compliance with ERCOT protocols 6.5.6 and 6.5.7, ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found at: http://www.ercot.com/gridinfo/generation/voltprof/index.html |
| 1 | When indicated, by SCADA alarms or when notified by a Transmission Operator of voltage concerns, TAKE appropriate action. |
| 2 | Use displays that contain voltages that are of concern. |
| 3 | INITIATE a solution in collaboration with the appropriate Transmission Operator and QSEs in the area. |
| NOTE: | ERCOT Nominal voltage levels are 345 kV, 138 kV and 69 kV. The general voltage guidelines are: Nominal Voltage (kV) Operating Limits (kV) Ideal Voltage Range (kV) 345 327.75 - 362.25 345 - 359 138 131.1 - 144.9 138 - 144 69 65.55 - 72.45 69 - 71.5 |
| NOTE: | When a VDI is given to a QSE requesting voltage support, the VDI will direct the QSE to maintain a specified voltage set point. The VDI shall not attempt to quantify the change in generator MW output necessary to maintain the voltage set point. |
| 4 | Instruction to a QSE to raise or lower bus voltage when area TOs have utilized all static Reactive Power Resources (capacitors, reactors, change in transformer taps): Typical script: “This is ERCOT operator [first and last name]. ERCOT is instructing [QSE] to raise or lower voltage at a [specified bus] by a stated number of kV (e.g., + 1 or 2 kV or – 1 or 2 kV). [QSE] please repeat this directive back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |

## 2.6.1	 Issue Verbal Dispatch Instructions (VDI)

Procedure Purpose: ISSUE a VDI to TO(s) to give a directive.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: August 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | VDIs should not re-iterate an instruction given via XML. |
| NOTE: | Whenever a VDI is issued, instruct the TO to repeat back the instructions. IF the TO Hotline is used to issue a VDI, direct all hotline participants to remain on the line until a hotline participant of your choice correctly repeats back to you the directive. If the repeat back is not acceptable, restate the instructions and direct a repeat back again. Continue until an acceptable repeat back is received. |
| 1 | As time permits, complete the VDI form (Desk Top Guide Section 7.4). The following are required fields on all VDIs: - VDI # - EXAMPLE: For the 4th VDI issued by the Transmission and Security Control Desk on May 01, 2009 the number would appear as “T-050109-4” - Operating Day - ERCOT System Operator - Receiving Entity - Receiving Entity’s Operator - Time & Date - Instruction - Reason for Instructions - Intervals - Repeated Instruction back - ERCOT Operator’s signature Blank fields are to have N/A entered. |
| 3 | LOG in the Operator’s Log the VDI information and information relevant to the decision for issuing the VDI. |
| 4 | Forward the VDI form to the Shift Supervisor, as time permits. |