## Power Operations Bulletin # 434

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.1.2	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | If RTCA or the State Estimator has not solved within the last 10 minutes, refer to Desk Top Guide Section 3.1 and run through the checklist. If, after trying all the checks and RTCA and/or the State Estimator still has not solved, notify the on-call State Estimator Support Engineer and request the tool(s) be restored to operation as soon as possible. If RTCA will not solve but the EMS is available notify the on-call Operations Engineer to request limits be calculated manually. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to the ERCOT Transmission Operators: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 30 minutes. Please monitor your own service area and notify ERCOT if thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits if power flows reach 85% of their respective limits. Continue to monitor voltages in your area. Notify ERCOT of any abnormal line operations in your area.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Once RTCA and State Estimator are operational: Make a Hotline call to the ERCOT Transmission Operators: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator are now functioning and we are now back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 4 | If VSAT has not solved within 1.5 hours: - Manually run VSAT - If no results, contact Operations Planning Support - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. - If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |

# 2.2.2 	Real Time Constraint Activity Manager (RTCAM)

Procedure Purpose: To alleviate congestion.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R4.2 | IRO-005 R1.2, R1.7, R3 | IRO-006 R1 |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | Local Congestion Management Techniques consist of OC3s, Unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| NOTE: | Phase shifters could at times be used to help with congesting management: - Putnam – NW/WN transfers to increase CSC transfer capability - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |
| Note: | To determine the Laredo Import utilize the RTCA results. In the event that RTCA is unavailable and RTMONI is available utilize the Laredo Import display to determine the import. Outages in the area may affect this and Operations Support will determine the import limit in those instances. |
| 1 | VERIFY SFT is enabled in the MOI. - This can be determined by making sure that the check box next to “Run SFT for Real-Time Markets” on the Real-Time Balancing Market display is checked. If it is not checked, then check it. |
| 2 | DETERMINE if RTNET and RTCA has solved within 10 minutes. |
| 3 | If RTNET and/or RTCA have not solved within 10 minutes, refer to Section 2.1.2, Analysis Tool Outages. |
| 4 | DETERMINE if RTNET has solved with a solution status of “VALID SOLUTION – NO SFT CASE.” - If RTNET has this solution, notify the State Estimator On-Call Engineer. |
| 5 | EXAMINE the RTCAM Branch Violations and Operating Constraints List. |
| 6 | EXAMINE the constraints with the “Active” check box filled in. - VERIFY that an OC3 is created for all overloaded active constraints in the MOI by selecting the “constraint” tab from the “Real-Time Balancing Market” screen in the MOI. In the Type column, sort descending. All OC3s will be sorted to the top of the page. - If an overloaded constraint is active in RTCAM, but the corresponding OC3 is missing from the MOI, LOWER the value in the “% Rating” column in RTCAM to tighten the constraint until the OC3 appears in the MOI. - If an OC3 is active in the MOI, but the corresponding constraint in RTCAM is well below the monitored rating, INCREASE the value in the “% Rating” column in RTCAM to loosen the constraint. |
| 7 | When an OC3 deploys quick start units for congestion, do one of the following: - Issue an “OOME VDI” for settlements on the quick start unit(s) that are required to mitigate congestion - Issue an OOME for quick start unit(s) using the OOM tool and keep the OC3 active, or - Use OOM tool to OOME for quick start unit(s) instead of activating an OC3, or - Issue a VDI to disregard the unit specific deployment and write “instructed deviation” on the VDI if congestion can be resolved without unit(s) OOME VDI for quick start units will only be given under the local congestion scenario, balancing and zonal deployments are not included. Follow up with a Settlements only VDI stating “OOME for Quick-start” on the VDI form. |
| 8 | To activate a constraint, check the “Active” check box next to the constraint to be activated. The text in this row of data will change to red and it will be immediately sorted to the top of the display. |
| 9 | To deactivate a constraint, uncheck the “Active” check box next to the constraint. Uncheck the “Retain” check box as well, if desired. Leaving the “Retain” box checked will only cause the constraint to remain on the Operating Constraints List display when an overload is not occurring. |
| 10 | To acknowledge constraints that are determined to be erroneous or are already accounted for, check the check box in the “Ack.” Column. This will sort the constraint to the bottom of the display. |
| 11 | Special Protection Schemes (SPS), Remedial Action Plans (RAP), and Pre-Contingency Action Plan (PCAP) analysis - EXAMINE the results in RTCAM for RAP or SPS activation, using the “SPS” and “RAP” columns on the Operating Constraints List display. - If “SPS” and/or “RAP” is checked, EXAMINE the color of the background. Refer to Desk Top Guide Section 3.3 for actions to be taken based on the color of the background. - ADJUST initial “% Rating” higher if activating a constraint for a post-RAP/SPS overload if needed. This is because RTCAM/SFT can not model RAP/SPS when generating OC3 constraints so they tend to over-constrain at 100 % of rating. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\departments\System Operations\Remedial Action Plans> |

# 2.2.4 	OOME when OC3 is not Effective

Procedure Purpose: A process to relieve congestion when an OC3 is not effective.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R2 | IRO-005 R1.7, R3 | IRO-006 R1 |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | All wind units have the non-bid flag checked in the Resource Plan which will prevent them from receiving local congestion instructions. When OC3 activation is not effective due to excessive wind generation output, the following steps shall be taken to OOME wind generation to relieve transmission congestion. |
| 1 | Activate an OC3 for local congestion as mentioned in Section 2.2.1. |
| 2 | Upon activation of the OC3, perform a Contingency Analysis study as indicated in Section 3.1 of the Desk Top Guide. |
| 3 | After performing a Contingency Analysis study, navigate to the Network Constraints Summary by going to Analyst Displays  Contingency Analysis Displays  Shift Factors, or typing NETSENS_CONSTRAINTS in the command line at the top of the display. |
| 4 | On the Network Constraints Summary Display, scroll to the constraint for which the corresponding OC3 was created. Click on the circle with an “i” inside it on the right hand side of the display. This will bring up the Network Constraints Details. |
| 5 | The Network Constraints Details display shows all units which have positive or negative shift factors above 1 % for the given constraint. Scroll through this list to find the wind units with the greatest positive shift factors. |
| 6 | The Group OOME tool should be used for local congestion involving wind only units. This will distribute MW amounts fairly when multiple units can solve the congestion. Notify Operations Support when a new group needs to be built. |
| 7 | If local techniques fail to maintain system security, an Emergency Notice must be declared before Zonal Techniques may be utilized. |

# 2.2.7 	West - North Dynamic Stability Limit

Procedure Purpose: To maintain West to North stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R2, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.7, R3 | IRO-006 R1 |
|  | TOP-002 R10 | TOP-007 R4 |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | If the current hour West-North Stability limit calculated on the W-N Stability spreadsheet changes in value or color, update the RTMONI limit on the “Stability-WN” monitor to the value shown on the spreadsheet. |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability.xls” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 3 | If the next hour Stability limit is significantly lower and reliability concerns exist that the stability limit may exceed the limit for more than 30 minutes, activating the OC1 may need to be implemented before 85%. |
| 4 | If the monitored flow on the Stability-WN monitor is approaching 85% and wind is climbing: - Activate the West – North OC1 - Change the W-N CSC limit to the Stability limit in RTMONI to give transparency to the Market. - Post a message on the MIS: Typical Script: “ERCOT is controlling the West - North Dynamic Stability Limit with the West – North OC1”. |
| 5 | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - OOME/VDI resource (Group or Single) - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control the West to North dynamic stability limit.” |
| NOTE: | If Zonal Techniques failed to control the West-North Stability limit and Local Congestion Management Techniques are being used, continue Zonal Techniques and release Local Congestion Management Techniques as soon as practical. |

# 2.2.8 	North-Houston Voltage Stability Limit

Procedure Purpose: To maintain North to Houston voltage stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R2, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.7, R3 | IRO-006 R1 |
|  | TOP-002 R10 |  |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| VSAT | Initiate a manual Run Sequence for the Network Online Sequence after the change in the system typology. This process will give new VSAT results after RTNET, RTCA and RTDCP (VSA) is completed. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | VSAT should be checked at least every hour, or more frequently as necessary. |
| Houston 345kV Outages | If North – Houston or South – Houston 345kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately then continue |
| Monitor | Monitor each of the following Reliability Margins: - O-HOUS_L - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TSP’s in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the North – Houston OC1 - Change the North – Houston CSC limit in RTMONI to the N-H VSAT Transfer Limit located in VSAT for Market transparency. - Post a message on the MIS: Typical Script: “ERCOT is controlling the North - Houston voltage stability limit with the North – Houston OC1”. |
| ≤300MW | If it appears that Zonal Techniques will fail to control the flow within 30 minutes, utilize Local Congestion Management Techniques. - OOME/VDI resource (Group or Single) - Post a message on the MIS: Typical Script: “ERCOT is controlling the North - Houston voltage stability limit with the North – Houston OC1”. |
| ≤200MW | - Fleet up in Houston area generation - Deploy Non-Spin in the Houston zone and utilize quick starts not bid in as Non-Spin - Post a message on the MIS: Typical Script: “Local congestion techniques are being utilized with Zonal congestion techniques to control North – Houston voltage stability limit.” |
| ≤100MW | Notify Frequency Desk to deploy LaaRs in Houston Zone. |
| 0MW ≥ 15 Minutes | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Post a message on the MIS: Typical Script: This is ERCOT operator [first and last name]. ERCOT is instructing Centerpoint to drop [*** MWs] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete and give the amount of load shed. Please repeat this back to me. That is correct, thank you.” |

2.2.11	SPS Monitoring

Procedure Purpose: To monitor and prevent an SPS operation if possible.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R4.2 | IRO-005 R1.1 |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | If notified to take a SPS in/out of service, ensure OPS Planning is notified. |
| NOTE: | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE: | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingent loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario congestion management is not needed until the criterion in Desk Top Guide Section 3.4 is met. |
| 1 | Special Protection Schemes (SPS) - EXAMINE the results in RTCA for SPS activation. - If “SPS” is identified as a post contingent overload, EXAMINE the color of the background. - Refer to Desk Top Guide Section 3.4 for actions to be taken based on the color of the background. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at <\\cpwp004d\departments\System Operations\Remedial Action Plans> |
| NOTE: | Typically SPS’s are to solve post-contingent overloads on the Transmission System. Due to outages, either (Planned or Forced) the Transmission topology is changed temporarily. During these conditions the ERCOT Transmission & Security operator(s) will utilize Congestion Management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | Monitor the Excel spreadsheet “Real Time Values” - Each SPS will be displayed, as the SPS activation threshold increases the display changes colors - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 3 | If the system operator receives a call from a TSP or as the threshold increases on the SPS to greater than 90%, then congestion management techniques should be employed in an attempt to prevent its’ activation. |
| NOTE: | If notified by a QSE that an SPS operates (runback or trip) refer to procedure: - 2.1.4 OOME – VDI Guidelines |

# 2.2.14 	Managing Line Rating Changes

Procedure Purpose: To obtain information on changes in line ratings.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002 R16 |  |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| 1 | When notified by a Transmission Operator of a line rating that is different from the ratings currently in RTNET, obtain the following information from the Transmission Operator: - Equipment ID Name - MVA ratings (Continuous, Emergency, and 15 Minutes) - Name of Operator on duty - Name of Transmission Operator (Company) - Name of Transmission Operator’s authorizing engineer - Authorizing engineer’s contact phone number |
| 2 | Continue to operate according to RTNET ratings. - Provide this information to the Shift Supervisor - Enter this information in the Transmission log under the “Line Rating Changes” log type |

# 2.5.3	Issue a Watch

Procedure Purpose: To inform the Market Participants of a Watch.

| Protocol Ref. | 5.6.5 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 4.2.3 |  |  |  |
| NERC Std. | COM-002 R2 | EOP-001 R4.1 |  |  |

| Approved by: |  |  | Effective Date: September 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| 1 | As directed by the Shift Supervisor, or when appropriate, ISSUE a Watch IF: - Transmission system conditions are such that ERCOT is expected to exceed limits with no practicable resource solution - A short supply, or congestion condition has been identified and no alternatives exist to relieve the condition - There is a hurricane in the Gulf with expected landfall in Texas - A cold front has arrived with temperature anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - Forced Outages or other abnormal operating conditions occur with no practicable resource solution - Adjusted Responsive Reserve drops below 2500 MW - A transmission condition has been identified that requires emergency energy from any of the South DC-Ties. |
| 2 | Issuance of a Watch requires: - Posting on the ENS - Posting on the MIS - Notifying TOs via the Hotline |
| 3 | Before issuing a Transmission Watch for transmission issues, notify the TO and discuss the actions you are about to take. |
| 4 | When issuing a Watch for a transmission issue, use the following script for making the hotline call: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission Watch due to the [planned or forced] outage of a generating unit causing the post contingency loss of (name of contingency) overloads (name of overloaded element).” |
| 5 | Typical MIS and ENS posting script: Transmission Watch issued due to the [planned or forced] outage of a generating unit causing the post contingency loss of (name of contingency) overloads (name of overloaded element).” |
| 6 | When issuing a Watch for other reasons, use the following script for posting the message and making the hotline call: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for [state Watch]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |