## Power Operations Bulletin # 440

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.1.2	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: September 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 6 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | If RTCA or the State Estimator has not solved within the last 10 minutes, refer to Desk Top Guide Section 3.1 and run through the checklist. If, after trying all the checks and RTCA and/or the State Estimator still has not solved, notify the on-call State Estimator Support Engineer and request the tool(s) be restored to operation as soon as possible. If RTCA will not solve but the EMS is available notify the on-call Operations Engineer to request limits be calculated manually. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to the ERCOT Transmission Operators: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 15 minutes. Please monitor your own service area and notify ERCOT if thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, and West - North and North – Houston stability limits if power flows reach 85% of their respective limits. Continue to monitor voltages in your area. Notify ERCOT of any abnormal line operations in your area.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Once RTCA and State Estimator are operational: Make a Hotline call to the ERCOT Transmission Operators: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator are now functioning and we are now back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 4 | If VSAT has not solved within 1.5 hours: - Manually run VSAT - If no results, contact Operations Planning Support - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. - If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |

# 2.2.3 	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R3.2, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.7, R3 | TOP-002 R10 |

| Approved by: |  |  | Effective Date: September 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 6 |  |

| Step | Action |
| --- | --- |
| NOTE: | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, and if a SPS, RAP, PCAP, TOAP, or MP does not exists; this is considered to be a potential IROL. Corrective action must be taken within 30 minutes to reduce the flow below 125%. |
| 1 | If congestion management techniques fail to reduce the flow below 125% within 30 minutes and no practicable resource solution exists, take real-time snap shot and save it so analysis can be done. Send an e-mail with the saved file name to: - OPS Support Engineering - 1 ERCOT Shift Supervisors |
| 2 | Notify the Shift Engineer or the on-call Operations Support Engineer, ask for a Mitigation Plan. |
| 3 | Make log entry. |

# 2.2.14 	Managing Line Rating Changes

Procedure Purpose: To obtain information on changes in line ratings.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002 R16 |  |  |  |

| Approved by: |  |  | Effective Date: September 3, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 6 |  |

| Step | Action |
| --- | --- |
| 1 | When notified by a Transmission Operator of a line rating that is different from the ratings currently in RTNET, obtain the following information from the Transmission Operator: - Equipment ID Name - MVA ratings (Continuous, Emergency, and 15 Minutes) - Name of Operator on duty - Name of Transmission Operator (Company) - Name of Transmission Operator’s authorizing engineer - Authorizing engineer’s contact phone number |
| 2 | The most limiting rating will be used until the correct rating can be determined. - Provide this information to the Shift Supervisor - Enter this information in the Transmission log under the “Line Rating Changes” log type |