## Power Operations Bulletin # 450

ERCOT has revised the Frequency Control Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.2.1 	QSE Hotline Test

Procedure Purpose: To test the communication systems for the QSE Hotline.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001 R2 |  |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Each Monday between 0630 and 1100 test the QSE Hotline. |
| 2 | Check with the Shift Supervisor and determine the ERCOT current threatcon level. |
| NOTE: | In the event of a failure of the Confertel software, the most recent printout of the hotline log may be used as a checklist to perform a manual roll call of QSEs. |
| NOTE: | Insure all “Lost Souls” are cleared prior to the hotline call. |
| 3 | Using the hotline, notify all QSEs of the purpose of the call. - When QSEs have answered the Hotline, print Hotline log. Typical script: “This is ERCOT operator [first and last name]. ERCOT is conducting the weekly QSE hotline test. We are currently at threatcon level [threatcon level]. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none in effect. This ends this test of the ERCOT Hotline. That is all.” |
| 4 | Notify the Shift Supervisor of any QSE that did not respond to the Hotline test. The Shift Supervisor and/or Help Desk may notify the telecommunications department for repairs. |
| 5 | Ensure printed Hotline log has date, time, and reason for call information. Forward to Shift Supervisor, as time permits. |

## 2.2.3 	Testing of Satellite Phone and NXT Communicator

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone System and NXT Communicator.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001 R2 | EOP-005 R5 |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
|  | Primary Control Center |
| NOTE: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in Section 7 of the Desktop Guide for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Section 7 of the Desktop Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | When testing is completed, fill out the portion of the Monthly Satellite Phone Conference Bridge Testing Form. An electronic copy of this form is located in P:\ SYSTEM OPERATIONS “Satellite Bridge Testing forms” folder. |
| 4 | When the applicable portion of the Monthly Satellite Phone Conference Bridge Testing Form is completed, save the form and close the file. Notify the Shift Supervisor that the Conference Bridge Call is complete and that the applicable portion of the form is complete. |
| 5 | Log the test date and results in the Operations Log. |
| 6 | Verify with the Shift Supervisor that the following personnel are notified for any Satellite phone problems during the test by e-mail: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |
|  | Alternate Control Center |
| 1 | When working out of the alternate control center during the monthly scheduled dates: - Test the Satellite phone - Test NXT Communicator by activating the “Test Message Monthly”. Refer to Desktop Guide 7.10 (Test early evening). If problems are encountered with the Satellite phone, follow step 6 above. If problems are encountered with NXT Communicator, open help ticket. |
| 2 | Log the test date and results in the Operations Log. |

# 2.3 	Weather & Load Forecasts

## 2.3.1 	Monitor Weather and Load Forecasts

Procedure Purpose: To monitor and update the weather and load forecasts due to bad or missing data.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: October 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | Validate the weather forecast data in EMS as needed to contribute to reliable system performance. Meteorlogix support is available 24 hours a day, seven days a week at (952) 882-4312. If the operator determines the EMS weather forecast is valid, no action is required. If the operator determines the EMS weather forecast is invalid: - Call Meteorlogix. - Call the Operations Planning Engineer supporting the LF application for support - E-mail the information to OPSPlanning@ercot.com as time permits . |
| 2 | EVALUATE Load Forecast as needed to contribute to reliable system performance. If the operator determines the load forecast is valid, no action required. If the operator determines an adjustment needs to be made to the load forecast: Before modifying data in the “Override” column to replace unsatisfactory or missing data; notify an Operations Planning Engineer supporting the MTLF application to adjust the load forecast accuracy. E-mail the information to OPSPlanning@ercot.com as time permits Reference Display: Load Forecast Study Results and History |
| NOTE: | Changes entered less than 45 minutes before the beginning of the Operating Hour might not be used by the Hour Ahead Study. |

## 2.6.10	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the alternate Control Center (ACC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001 R5 | EOP-001 R4.4 | EOP-008-0 | IRO-005 R1.10 |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 7 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC (cell phone or PBX Bypass phones), THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT is declaring an emergency and is transferring operations to the alternate control center. Until further notice, direct all urgent phone calls to (512) 225-7100. [Select QSE], go on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last good interval]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat this directive back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT declaring an emergency and is transferring operations to the alternate control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT if thermal limits reach 85% of their continuous rating. Report zonal CSC transfers, West - North and North – Houston stability limits if power flows reach 85% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat this directive back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Issue a VDI to the QSE that was put on constant frequency, as time permits. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached 85% of their continuous rating, - Zonal CSC transfers have reached 85% of the last posted limit, - West-North stability limit has reached 85% of its limit,, - North-Houston stability limit has reached 85% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for the stability limits, - Continue to monitor the thermal limits and zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the thermal limits and/or zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 85% (IROL) | IF: - The West-North stability limit is approaching 85% and is continuing to trend upward, - The North-Houston stability limit is approaching 85% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 85% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Zonal Transfers and thermal Limits Reached 95% (SOL) | IF: - Thermal limits have reached 95% of their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.6.11	Restoration of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Frequency Control Desk Operators at the alternate Control Center (ACC) in restoring Real-Time operations.

- Additional staff has arrived, including a Shift Supervisor,

- ACC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | As additional Operators arrive, be sure to communicate any pertinent information that will assist them in getting their specific functions ready for normal operation. |
| Restoring Frequency Control | When an Operating Period Desk Operator has arrived, had time to get the offset calculation spreadsheet caught up, and is able to enter offset values into the MOI: IF: - Holding Real-time Balancing Energy Market (RTB) deployments, THEN: - Verify the proper operation of the RTB and that deployments are being sent to the Market Participants (MP) AND - Remove the QSE that is put on constant frequency. |
| Market Notification | IF: - RTBM is running and valid deployments are being sent, THEN: - Place the following QSE Hotline call: * * * WARNING * * * When removing a QSE from constant frequency control, remove ERCOT AGC from Monitor mode. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT is resuming normal, Real-Time operations from the alternate control center. Please continue to direct all phone calls to (512) 225-7100. ERCOT is ending VDI [#] at [time]. Resume with the [interval ending time] Balancing Energy deployments. [Select QSE], “Please repeat this directive back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Additional Notifications | Notify the following: - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations and/or designee - Engineering Support - These phone numbers have been programmed into the control room cell phone. |
| Notification of Additional Operators | WHEN: - All functionality has been resumed at the ACC, THEN: - Notify the additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System. |
| Contact Security | Notify Security that the transition of Operations to the ACC has been completed |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |