## Power Operations Bulletin # 452

ERCOT has revised the Shift Supervisor Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

2.2.10	PUCT Daily Report

Procedure Purpose: To provide ERCOT system transparency to the PUCT staff and Market Participants

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R4.1, R5 |  |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | The PUCT reports are to be generated twice per day: In winter months at 0100 and 0500 In summer months at 1100 and 1500 The timing change will be determined by the Manager, System Operations. |
| NOTE: | Be able to provide a list of unplanned generation outages for the day if requested by the PUCT. |
| 1 | Complete the PUCT Daily Report template at the appropriate times. In the “Important Comments” column add the forecasted peak hour. E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Do not add editorial comments to this report that reveal market sensitive data. General comments that convey overall system conditions are allowed. |
| 2 | Revise the last report sent and resend it if: - The probability of an EEA event increases. Give reason(s) for escalation - Conditions change that required new notices to be issued or cancelled, such as, an OCN , Advisory, Watch, or Emergency Notice - A projected reserve capacity shortage develops - Local reliability concerns arise which include actual overloads and/or loss of load, especially the Laredo area - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if there are unplanned outages of the generation units in the area. - Localized gas restrictions, not expected to cause reliability issues. - DCS event occurs - “ERCOT only” NERC and/or DOE event occurs. These events are market sensitive so provide a brief description without the market sensitive information. When issuing Transmission Watches or Emergency Notices use the following language: “At [time], ERCOT issued a Transmission [Watch or Emergency] due to the [planned or forced] outage of a generating unit causing the post contingency of [name of contingency] would overload [name of overloaded element].” |
| 3 | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves. - Medium - A Watch is in effect for Adjusted Responsive Reserves and/or - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves and/or - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Adjusted Responsive Reserves and trending downward after procuring quick-start capacity and/or - Excel MAI shows multiple hours of insufficient reserves and ERCOT has been unable to correct the capacity insufficiency over several hours and ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect |
| 4 | Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Adjusted Responsive Reserves - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect |
| 5 | Potential for EEA Level 2B - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical EEA Level 2B in effect |
| 6 | Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B (if available) in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |
| NOTE: | When conditions have returned to normal, update report and e-mail. |

## 2.7.6	Loss of Primary Control Center Functionality

Procedure Purpose: To maintain grid reliability during the loss of the primary control center.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R5 | EOP-008 R1.4 |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| 1 | It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of Control Center personnel. |
| 2 | Upon confirmation of imminent danger to Control Center personnel immediately evacuate the Control Center to a secure area, taking the Control Center cell phone and a copy of this procedure with you. |
| NOTE: | After the Control Center has been evacuated the Shift Supervisor may: - Re-locate the entire shift to the Alternate Control Center (ACC). - Send a partial shift or contact extra personnel to report to the ACC. - Remain in the secure area in anticipation of a quick return to the Primary Control Center (PCC). - The Shift Supervisor may choose another course of action that will best maintain grid security depending on the circumstances causing the evacuation. |
| 3 | The Shift Supervisor is responsible for the following notifications in the event of a Control Center evacuation. Information and instructions conveyed will be based on the Shift Supervisor’s decision regarding relocation to the ACC. - Frequency Desk Operator at the BCC - ERCOT Security TCC1 – Ext. 3000 - ERCOT Security TCC2 – Ext. 6400 - ERCOT Security ACC – Ext. 7000 - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations - Engineering Support These phone numbers have been programmed into the control room cell phone |
| NOTE: | - The Frequency Desk Operator at the BCC will be responsible for all notifications if there is a loss of the PCC and he/she has not been contacted by the Shift Supervisor. |
| NOTE: | Once additional staff members have arrived, including a Shift Supervisor at the ACC: - Refer to Frequency Desk Procedure: 2.6.11 Restoration of Primary Control Center Functionality |

2.7.7	Monthly Testing of Satellite Phone System

Procedure Purpose: To test the satellite phone system between ERCOT and the ERCOT Transmission Operators to ensure communication capability via the Satellite Phone.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001 R2 | EOP-005 R5 |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE | - This test is to be conducted on the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday. - Not all ERCOT Transmission Operators have satellite phones; therefore the call will be coming in on their regular landlines. Verify whether or not they are communicating via satellite phone or regular landline while testing. - Refer to the ERCOT Satellite Phone User Guide located in the Desktop Guide |
| TEST | - Call each Transmission Service Provider using the preprogrammed number on the Turret Phone. Refer to page #2 of the ERCOT Satellite Phone User Guide for instructions. If there is no answer: Call the Transmission Service Provider directly using the Satellite Phone number provided in Section 7 of the Desktop Guide. - As contact is made with each Black Start Transmission Service Provider, establish a time when a Satellite Conference Bridge Call will be made from the appropriate ERCOT Operations Desk. Refer to Section 7 of the Desktop Guide for a list of Transmission Operators, Satellite phone numbers and Moderator Pass Codes for each ERCOT Operations Desk. |
| FORMS | When testing is completed by all desks, fill out Monthly Satellite Testing forms located in P:\ SYSTEM OPERATIONS “Satellite Testing Phone Testing Forms” folder. |
| FILE | File a hard copy in the control room. |
| LOG | Log the test date and results in the Shift Supervisors Operations Log. |
| E-MAIL | - Send the compiled results of the Satellite phone test by e-mail to: - 1 ERCOT Training Department - 1 ERCOT Shift Supervisors |

## 2.7.8	Monthly Testing of Non-Routinely used Telecommunications Facilities

Procedure Purpose: To ensure backup communications are tested monthly.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R2 |  |  |  |

| Approved by: |  |  | Effective Date: December 1, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
|  | Primary Control Center |
| TEST | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday: - Test the Control Room Cell Phone by calling the ERCOT Helpdesk Cell Phone. - Test the Standalone Satellite phone. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Desktop Guide 7.9.4. - Test NXT Communicator by activating the “Test Message Monthly”. Refer to Desktop Guide 7.10. |
|  | Alternate Control Center |
| TEST | When working out of the alternate Control Room during the monthly scheduled dates: - Test Control Room Cell Phone with the ERCOT Helpdesk Cell Phone. - Test the Satellite phone associated to the Operations Desk on each turret. It isn’t necessary to call a satellite number, just verify the phones are operational. - Test the Standalone Satellite phone operation located in the Control Room. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Desktop Guide 7.9.4. - Test NXT Communicator by activating the “Test Message Monthly”. Refer to Desktop Guide 7.10. |
| LOG | Log the test date and results for each of the bulleted items above in the Shift Supervisors Operations Log. If problems are encountered with NXT Communicator, open a help ticket. |