## Power Operations Bulletin # 458

ERCOT has revised the Day-Ahead Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.7	Procure Ancillary Services (DRS, URS, RRS, NSRS) in Day Ahead

Procedure Purpose: Procurement of the Ancillary Service Market and what to do it timeline is not met.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002 R1, R5 |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| 1 | Between 1315 and 1330, CALL-UP the “Ancillary Service Markets” display. |
| 2 | VERIFY that the correct date for the operating day is selected. |
| 3 | SELECT “Execute.” |
| 4 | When execution is complete, REFRESH display (F8). If procurement of Ancillary Services is not complete by 1330, proceed to Step 6. |
| 5 | Review and Approve, refer to procedure section 2.8. |
| 6 | If the procurement of Ancillary Services is not completed by 1330, issue an Market Emergency Notice to QSEs, using the hotline: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Market Emergency Notice. Procurement of Ancillary Services has not met the time requirement. ERCOT will notify you when more information is available. [QSE] please repeat this back to me. That is correct, thank you.” - Post the following message on the MIS and ENS: - A Market Emergency Notice issued due to the procurement of Ancillary Services has not met the time requirement”. |
| 7 | Once the procurement of Ancillary Service is complete, terminate the Market Emergency Notice to QSEs, using the hotline: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. The procurement of Ancillary Services has completed. ERCOT is terminating the Market Emergency Notice. [QSE] please repeat this back to me. That is correct, thank you.” - Update messages on the MIS and ENS: - MIS – Make Market Emergency Notice invalid. - ENS – Enter end time for Market Emergency Notice. |

## 2.8	Review the Ancillary Services Market Clearing Data

Procedure Purpose: Verify Ancillary Service Market has cleared with no shortages.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005 R1.4 |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | A capacity shortage is significant if it cannot be accounted for by system rounding errors or known problems in ERCOT or QSE systems. |
| 1 | Check for any significant capacity shortage for any hour for DRS, URS, RRS, and NSRS. MOI: “Ancillary Service Markets” – “Ancillary Service” tab: If a capacity shortage exists for any ancillary service for any hour, THEN CONTINUE; OTHERWISE, GO TO Step 3. |
| 2 | If any significant shortages exist for any Ancillary Service, notify the Shift Supervisor and Market Operations personnel. Issue a Watch to QSEs, using the Hotline: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch. [Ancillary Service(s)] bids were insufficient for [MM/DD/YYYY], hour(s) ending [HE]. ERCOT will [open a second Ancillary Service Market] or [procure additional capacity]. [QSE] please repeat this back to me. That is correct, thank you.” Post message on the MIS and ENS: - MIS – “A Watch has been issued due to insufficient [Ancillary Service(s)] bid for [MM/DD/YYYY], hours ending [HH].” - ENS – “Watch for Insufficient Ancillary Service bids, see MIS”. IF adequate Emergency Short Supply Services are procured, THEN TERMINATE the Watch. OTHERWISE, CONTACT the Shift Supervisor for resolution. |
| 3 | Once the shortage(s) of Ancillary Service has ended, terminate the Watch to QSEs, using the hotline: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is terminating the Watch for insufficient Ancillary Services. [QSE] please repeat this back to me. That is correct, thank you.” - Update messages on the MIS and ENS: - MIS – Make Watch Notice invalid. - ENS – Enter end time for Watch Notice. |
| NOTE: | A MCPC value may be considered questionable if it does not follow a reasonable trend when compared to the values immediately preceding or following such a value or a sudden unexplained change occurs in the magnitude of values at any time. |
| 4 | REVIEW the Market Clearing Prices for Capacity for each hour of the operating day for DRS, URS, RRS, and NSRS. IF any MCPC values appear questionable, GO TO next Step. OTHERWISE, DONE. MOI: Ancillary Services Market display; Ancillary Services tab; OR http://mospublic.ercot.com/ercot/jsp/ancillary_services_mcp.jsp; and select operating day. |
| 5 | DISCUSS with the Shift Supervisor and Market Operations Support personnel. IF it is determined that one or more MCPC values are questionable: Post message on the MIS and ENS: - MIS – “The MCPC for [ancillary service] for hour [hour] on [day and date] has been deemed questionable by ERCOT. Appropriate ERCOT personnel will review the posted value.” - ENS – “MCPC questionable for [hour] on [DD/MM/YY], see MIS”. |

## 2.10	Procure Additional Ancillary Services (DRS, URS, RRS, NSRS) during the Adjustment Period

Procedure Purpose:  Additional A/S needed in the Adjustment Period

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005 R1.4 |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| 1 | If following the close of the Day-Ahead Market, conditions develop such that additional Ancillary Services may be needed, DISCUSS with the Shift Supervisor. If it is determined that an additional market is NOT needed, then LOG the decision and continue with normal duties. OTHERWISE, CONTINUE. |
| NOTE: | The Shift Supervisor should consult with the appropriate Manager and Market Operations Support to decide if opening an Adjustment Period market for additional Ancillary Services is appropriate. Remember that QSE’s scheduling BESCNSRS into the BES market must adjust their NSRS Resource and Obligation schedules by the amount that is supplied by BESCNSRS and must provide BES Up bids after the Ancillary Service market clearing. |
| NOTE: | Time X in this procedure is the start of the clock hour after it is determined that an additional Ancillary Services market is appropriate. |
| 2 | By Time X (no less than three hours prior to the start of the Operating Hour that the Ancillary Service capacity is required), using the hotline, notify QSEs: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch. Additional Ancillary Services are needed. At [X+60] ERCOT will open an Adjustment Period Ancillary Services market for [applicable services] during the hours of [applicable hours]. Bids eligible for removal may be removed between [X] and [X+60]. [QSE] please repeat this back to me. That is correct, thank you.” - Post message to MIS: ERCOT issued a Watch. Additional Ancillary Services are needed. At [X+60] ERCOT will open an Adjustment Period Ancillary Services market for [applicable services] during the hours of [applicable hours]. Bids eligible for removal may be removed between [X] and [X+60]. - Post message to ENS: “Watch – Insufficient Ancillary Services, see MIS” |
| 3 | At <X+55> CREATE a new Ancillary Services market. - SET the start and end times for the market to match the period for which additional Ancillary Services are needed. - SET the bid open time equal to <X+60>. SET the bid close time equal to <X+90>. - INCREASE the amount of Ancillary Services to equal the quantity from the previous market plus the additional amount required for applicable services during the applicable hours except for NSRS. For NSRS you must increase the requirement the amount of the requirement that you are short plus any additional amount required. Example: Previous market requirement + additional quantity needed = quantity to enter. NSRS example: Previous market requirement – scheduled + difference + additional quantity needed = quantity to enter. |
| 4 | At <X+60> PUBLISH Ancillary Service Obligations. |
| 5 | At <X + 90>, PROCURE and APPROVE this market. |
| 6 | CHECK that QSE schedules are updated. If not, then REQUEST that the schedules be updated by one hour after market clearing. |
| 7 | - About one hour after market clearing, VERIFY that no Ancillary Service deficits exist. - A Resource Plan Validation Study may be run if desired. - If deficits exist, notify Shift Supervisor and/or Market Operations Support. |

## 2.15	Initiate Adjustment Period Replacement Market

Procedure Purpose:  Additional generation needed in the Adjustment Period

| Protocol Ref. | 4.5.6 | 6.6.3.2.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | If either the Excel MAI or the results of section 2.13 indicates that an additional Replacement MARKET is needed, DISCUSS with the Shift Supervisor. Time permitting, NOTIFY the Shift Supervisor if the projected shortage is based on a reasonable load forecast and a potential capacity shortage still exists on Excel MAI after an Adjustment Period Replacement Capacity STUDY completes. If it is determined that a second Market is needed, CONTINUE. |
| NOTE: | In the following steps, “X” designates the time at which the need for additional RPRS is identified (adjusted to the top of the next clock hour). Protocol requires no less than two hours, but that has proven to be impractical. |
| 1 | At least 10 minutes prior to time X, but no less than three hours prior to the start of the first Operating Hour that the additional Replacement Reserve Services are required, OPEN a RPRS market by selecting the PUBLISH button on the Study page for the appropriate hours through hour ending 2400 of the day of the study. |
| 2 | AT time X, ISSUE a WATCH using the hotline, notify QSEs: - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. As time permits, notify the Shift Supervisor of any issues during the call. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch. Conditions have developed that additional Replacement Reserve Services are needed. At [top of hour], ERCOT will open an Adjustment Period Replacement market for the remainder of the day. QSEs have 30 minutes to update their schedules. ERCOT reminds Wind QSEs to update their resource plans with the latest AWS Truewind forecast. [QSE] please repeat this back to me. That is correct, thank you.” Post message on the MIS and ENS: - MIS – “ERCOT has issued a Watch. Additional Replacement Reserve Services are needed. At <top of clock hour> ERCOT opened an Adjustment Period Replacement market for the remainder of the day. QSE’s have 30 minutes to update their schedules before ERCOT purchases additional Replacement Reserves. Wind QSEs are reminded to update their resource plans with your latest AWS Truewind forecast.” - ENS – “Watch for Adjustment Period Replacement Market, see MIS”. |
| 3 | At time X+ 45 minutes, RUN a replacement analysis by clicking the “EXECUTE” button. |
| 4 | Review Analysis Results - Do NOT deselect any RMR units selected by the RPRS study unless there is a valid reason. Use the study selections to provide an Updated Final RMR Delivery Plan to the appropriate QSE. - Refer to Outage Coordinator Notes for unit requirements due to outages and compare with RRS results - If STEP 1 (local congestion) of the RPRS study has selected a steam turbine (ST) from a combined cycle train which requires a combustion turbine (CT) from the same train to be online, it is acceptable to OOMC that CT if it was not already expected to be online or procured. - If Step 2 (zonal congestion and capacity) of the RPRS study has selected a steam turbine from a combined cycle train which requires a combustion turbine from the same train to be online, the market participant must bring on the necessary CT on their own without an OOMC, because resources are usually procured by bids in Step 2. - In Step 1 or Step 2, if the RPRS study has selected a combustion turbine (CT) from a combined cycle train which requires a steam turbine (ST) from the same train to be online, it is acceptable to OOMC a ST if it was not already expected to be online or procured. - Investigate discrepancies, if any. - Review Transmission operator security requirements as received and compare with RPRS results. Request confirmation of the requirements by Operations Engineering if something new or a significant change is seen in the RPRS study results. - De-select additional units for each hour if you know they are not needed. If de- selecting a unit, do NOT replace a de-selection with an OOMC unless you are substituting with another unit for a justifiable reason. |
| 5 | Execute RPRS Step 3 (Pricing). |
| NOTE: | A MCPC value may be considered questionable if it does not follow a reasonable trend when compared to the values immediately preceding or following such a value or a sudden unexplained change occurs in the magnitude of values at any time. Inform Market Operations Support of questionable MCPC values. |
| 6 | By time X + 60, review the solution of the Replacement Capacity analysis for reasonableness. - If reasonable, APPROVE, and task is complete. OTHERWISE, CONTINUE If not reasonable, discuss with Operations Support. If the consensus is that the results are not reasonable, then, click UNAPPROVE. |
| 7 | Following any procurement or non-approval of replacement capacity, determine the OOM/RMR units to be manually dispatched if the market cannot resolve a capacity shortage. - IDENTIFY any expected capacity shortages for any hour(s) of the operating day. - IF a capacity shortage for a given hour is insignificant (i.e., less than 100 MW), RECOMMEND to the Shift Supervisor that it be observed during the adjustment period for possible correction. - IF the shortage is significant (i.e., greater than 100 MW), and there are no constraints, OOM enough capacity in any zone to make up the shortage for the hours needed. Minimize starts in the OOMC process. |

## 2.22	Restoration of Primary Control Center Functionality

Procedure Purpose:  This procedure is to be performed by Day-Ahead Desk Operator at the alternate Control Center (ACC) in restoring Day-Ahead Market functions.

- Essential staff has arrived,

- ACC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4.0 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Prior to Resuming Day-Ahead Market | Upon arrival to the ACC: - Check with the Frequency Control Desk Operator to find out about any calls received from QSEs and if any VDIs were issued, - Check with Operating Period Desk Operator to find out if RTBM deployments have resumed. |
| Market Notification | When you are ready to resume normal operation, place the following Hotline call to the QSEs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT is resuming normal, Day-Ahead Market operations, from the alternate control center. Until further notice, direct all Day Ahead Market phone calls to (512) 225-7102.” [Select QSE], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |