## Power Operations Bulletin # 460

ERCOT has revised the Operating Period Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.6	Restoration of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operating Period Desk Operator at the alternate Control Center (ACC) in restoring Real-Time operations.

- Additional staff has arrived,

- ACC has become PCC,

- All EMS applications up and functioning properly

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: February 2, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 3.0 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Prior to Resuming Hour Ahead Functions | Upon arrival to the ACC: - Check with the Frequency Control Desk Operator to find out about any calls received from QSEs and discuss any issues, - Check with Transmission and Security Desk Operator to find out if any VDIs have been issued that may show QSE shortages as studies are resumed, - Take the necessary steps to get the Offset Spreadsheet caught up, start calculating and entering in Offsets into the MOI, |
| Market Notification | IF: - You have determined that valid deployments are being dispatched and you are ready to resume normal operation, THEN: - Notify the Frequency Control Desk Operator that normal deployments are being dispatched and he/she can make their Hotline call to the QSEs to resume normal operation. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |