## Power Operations Bulletin # 467

ERCOT has revised the Frequency Control Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.3	Roles/Responsibilities

ERCOT Shift Supervisor

The ERCOT Shift Supervisor is responsible for supervision of the ERCOT Frequency Control Desk position and may at times be responsible for performing the procedures contained in this manual.

ERCOT System Operator, Frequency Control Desk

The ERCOT System Operator – Frequency Control Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT electric system.  These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

## 2.1.1 	Capacity and Reserve Monitoring

Procedure Purpose: To ensure the required amount of operating reserves are available to meet the load forecast.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002 R2.4 | IRO-005 R1.4, R1.5, R4 |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 3 |  |

| Step | Action |
| --- | --- |
| 1 | Monitor the current ERCOT System Load and Short Term Load Forecast. Reference Displays: Generation Area Status Short-Term Load Forecast Excel MAI (Market Analysis Interface) |
| 2 | Determine that the current ERCOT System generation capacity is sufficient to meet the Short-Term Load Forecast requirements. Reference Displays: Generation Area Status Excel MAI (Market Analysis Interface) |
| 2a | Compare the current generation and load with the planned capacity values from resource plan at least every other hour. Reference Displays: Generation Area Status Daily Operation Plan – Resource Plan Excel MAI (Market Analysis Interface) |
| 2b | When QSE’s representing WRG’s notify ERCOT of possible icing, ask them to reflect that in their resource plans. |
| 2c | If real-time generation is approaching planned capacity a possible reserve capacity shortage is developing. Discuss situation with Operating Period Desk and Shift Supervisor, and increase monitoring of reserves. Reference Displays: Generation Reserve Status – Available Details Real Time Balancing Market – Balance Bid Tab Real Time Balancing Market – QSE Tab Excel MAI (Market Analysis Interface) |
| 3 | If a projected reserve capacity shortage is developing in the next hour, consider OOMC or deploying of Non-Spinning Reserve Service. Consult with the Operating Period Desk regarding hour-ahead study results. |
| 4 | If OOMC is decided upon, request the Transmission & Security Desk perform the actual instruction. If NSRS is decided upon, request the Operating Period Desk perform the actual instruction. |
| 5 | MONITOR additional available generation capacity and available DC tie capacity. Evaluate amount of additional capacity available in a short time frame using telephone communications to QSEs as appropriate. Reference Displays: Generation Area Status Generation Reserve Status Generation Tie-Line Status |
| 6 | Monitor Responsive Reserves on the QSE Reserve Status Display. If Adjusted Responsive Reserve plus LaaRs is correctly calculated, and is below 2300 MW, - notify the Shift Supervisor - implement EEA - log in the Operator’s Log any decision to declare an EEA |
| 7 | Monitor Ancillary Service Obligations. If a QSE is not meeting its Ancillary Services obligations as shown on the QSE Reserve Status Display, - contact the QSE to correct the deficiency - notify the Shift Supervisor of the QSE’s response - log the activities performed in connection with this step |
| NOTE: | Due to generation minimum down time, if NSRS is deployed and has ended, it would be acceptable for a QSE to keep their unit(s) providing non-spin on-line at its LSL. If NSRS is deployed again, it would need to move to its HSL. |

## 2.1.5	VDI Guideline to Relieve QSEs from Ancillary Service Obligations

Procedure Purpose: To relieve a QSE of their Ancillary Service obligations when they receive a prior dispatch instruction.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. |  |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| 1 | When a QSE receives a dispatch instruction that will prevent them from meeting their Ancillary Service obligation, choose one of the following options: - Upon a QSE’s request (coordinate with the Transmission desk), issue a VDI to relieve the QSE from their Ancillary obligation, OR - Coordinate with the Transmission desk to release the QSE from the dispatch instruction so they can come back into compliance. Note: If relieving a QSE from Non-Spin obligation, issue a VDI whether the service has been deployed or not. |

## 2.4.1 	Monitor SCE for each QSE

Procedure Purpose: To ensure that QSE’s Schedule Control Error is maintained within acceptable limits and the telemetry is working correctly.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-005 R14 | IRO-005 R1.6 |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| 1 | Compare QSE’s SCE with the ERCOT calculated SCE. If these two values differ significantly, and the cause is not known, review SCE components with the QSE to determine the source of the disagreement. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 2 | When the source of disagreement is established, decide which end (QSE or ERCOT) is most likely in error. If the error is on the ERCOT end, call technical support if appropriate. If the error is on the QSE end, instruct that the QSE take corrective action and/or develop a plan to mitigate the problem. Reference Displays: Responsive, Regulation, and SCE – SCE Calculation Responsive, Regulation, and SCE – SCE Calculation – Details |
| 3 | Monitor QSE generation and SCE: - Remove a QSE’s SCE feedback if they have a large SCE and their generation is not moving in the proper direction or rate to correct their SCE. - If SCE for a QSE departs significantly from 0 for an unknown reason, or if a SCE violation is causing a reliability problem, call the QSE involved and determine the reason for the deviation. - If a wind only QSE SCE deviates significantly from 0, call the QSE and instruct them to update their resource plan and base power schedules. The resource plans and base power schedules should be updated together and stay matched. Since base power changes are not allowed during the operating hour the SCE cannot be corrected immediately. Reference Display Responsive, Regulation, and SCE Regulation |
| 4 | NEVER (unless directed by the Control Engineer or designee): - Modify “Total (SCE-responsive) Feedback Gain” (should be altered by the Control Engineer) - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) Reference Displays: Responsive, Regulation, and SCE – Details |

## 2.4.4 	Review AGC Performance

Procedure Purpose: To maintain NERC Control Performance Standard 1 compliance.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-005 R2 | EOP-002 R6 | NUC-001 R4.2 |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| GOAL: | Maintain CPS1 over 100. Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Ancillary Service Performance Monitor – Regulation Services Note: Nuclear Power Plants do not run in AGC Mode. |
| 1 | If performance drops below 100 for over three consecutive hours, attempt to identify the reason. Actions that may be taken are: - Check Regulation Service available during the time frame. - If Regulation Service was depleted check with Operating Period Desk and inquire if enough Balancing Energy had been deployed to restore Regulation Service. - If Regulation Service was depleted check for QSEs with large SCE in the direction of the depleted Regulation Service. If the cause for the large SCE is unknown contact the QSE and inquire about the status of their SCE. |
| 2 | LOG in the Operator’s Log the event and the probable cause of the poor performance. |

## 2.5.1	Frequency Control Operating Procedure

Procedure Purpose: To maintain system frequency within acceptable levels.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002 R6, R7, R8 | BAL-005 R6 | BAL-007 | NUC-001 |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency id greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 600 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -600 MW |
| Response to High Frequency |  |
| BAAL SHEET | Open realtime on ‘erpfileb’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| MONITOR | Frequency above 60.05 and continuing to climb or over 60.05 > five minutes: - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. - Check to ensure available Down Regulation. |
| 10 MINUTES | If 10 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Call QSEs with positive SCE and instruct them to reduce generation to return their SCE to zero as soon as possible. - If out of Down Regulation, issue fleet down instruction to a QSE with sufficient Down Regulation (see script below). Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain 0 SCE) to reduce generation. Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#] to [QSE]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this back to me. That is correct. I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 15 MINUTES | If 15 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Call the QSE with the positive SCE and explain to them that their dispatch is causing the high Frequency resulting frequency to be higher than NERC BAALHigh trigger limit. Instruct the QSE with the positive SCE to bring their SCE back to zero within 10 minutes. - Issue fleet down instructions to additional QSEs with Down Regulation room (see script above). - Log the event and notify Shift Engineer. - Shift Engineer will send the event notification via email to BAALfieldtrials@ercot.com |
| 20 MINUTES | If 20 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Call the QSE with the positive SCE and explain to them that their dispatch is causing the high Frequency resulting frequency to be higher than NERC BAALHigh trigger limit. Instruct the QSE with the positive SCE to bring their SCE back to zero within 5 minutes. - Log the event and actions undertaken to bring the frequency below BAAL trigger limit. |
| 25 MINUTES | If 25 consecutive minutes of ACE above BAALHigh (60.09 Hz): - If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE or no QSE appears to be hanging out or no physical regulation down service is available. - Issue fleet down instructions to additional QSEs with Down Regulation room (see script above). - Log the event and actions undertaken to bring the frequency below BAAL trigger limit. |
| STABLE | Once regulation is restored and frequency is stable, end fleet down generation instruction: Typical script: This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time]. This ends the fleet down instruction. Please repeat this back to me. That is correct, thank you.” |
| Response to Low Frequency |  |
| BAAL SHEET | Open realtime on ‘erpfileb’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| MONITOR | Frequency below 59.95 and continuing to drop or below 59.95 > 5 minutes: - Remove SCE feedback from QSEs with negative SCE and monitor frequency response. - Consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. - Check to ensure available Up Regulation. |
| 10 MINUTES | If 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with negative SCE and monitor frequency response. - Call QSEs with negative SCE and instruct them to increase generation to return their SCE to zero as soon as possible. - Responsive Reserve (Contingency Reserve) will deploy to bring back the frequency within normal range. |
| 15 MINUTES | If 15 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are being sent out. - Remove SCE feedback from QSEs with negative SCE. - Explain to the QSE with the negative SCE that their dispatch is causing the low Frequency resulting frequency to be lower than NERC BAALLow trigger limit. Instruct the QSE with the negative SCE to bring their SCE back to zero within 10 minutes. - Issue fleet up instruct to QSE with Up Regulation room (see script below). - Log the event and notify Shift Engineer. - Shift Engineer will send the event notification via email to BAALfieldtrials@ercot.com. Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain SCE) to increase generation. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#] to [QSE]. Increase your fleet generation by [MW amount] due to low frequency. Please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. Increase your fleet generation by [MW amount] due to low frequency. Please repeat this back to me. That is correct; I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 20 MINUTES | If 20 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with negative SCE. - Explain to the QSE with the negative SCE that their dispatch is causing the low Frequency resulting frequency to be lower than NERC BAALLow trigger limit. Instruct the QSE with the negative SCE to bring their SCE back to zero within 5 minutes. Get an update on dispatcher actions and corrective actions being taken. - Issue fleet up instruct to additional QSE(s) with Up Regulation room (see script above). - Log the event and actions undertaken to bring the frequency above BAAL trigger limit. |
| 25 MINUTES | If 25 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE or no QSE appears to be hanging out or no physical regulation down service is available. - Issue fleet up instruct to additional QSE(s) with Up Regulation room (see script above). - Log the event and actions undertaken to bring the frequency above BAAL trigger limit. |
| STABLE | Once regulation is restored and frequency is stable, end fleet up generation instruction: Typical script: This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time] This ends the fleet up instruction. Please repeat this back to me. That is correct, thank you.” |
| CRITERIA | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes. - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes. - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes. Individual performance will be assessed Level 0 if ACE exceeds the BAAL for more than 30 consecutive clock-minutes. |
| NOTIFY | If it is recognized that frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| Loss of Frequency Control |  |
| EMS ISSUES | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or PAUSED or - “Last AGC Cycle” time on Generation Area Status display is not updating, or - AGC operation adversely impacts the reliability of the Interconnection Place a large QSE (that has regulation reserve) on constant frequency, by issuing a VDI. |
| MONITOR MODE | - In the scenario where AGC operation adversely impacts the reliability of the interconnection, (ERCOT is handing over the frequency control to a large QSE), ERCOT AGC should be placed into the MONITOR mode. |
| QSE HOTLINE | Using the Hotline, notify all QSEs that ERCOT is having computer issues and is putting a QSE on constant frequency. - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is currently having computer issues and has put a QSE on constant frequency until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| TO HOTLINE | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| FLEET | If the QSE that is put on constant frequency is having trouble keeping up, issue fleet VDI’s to other QSE’s to help out or put a different QSE on constant frequency. Remember to take the first QSE off constant frequency. |
| QSE HOTLINE | When frequency control is functional, remove QSE from constant frequency. Notify all QSE’s by Hotline that ERCOT is back on control. - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is back to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| TO HOTLINE | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| LOSS OF EMS OR SITE FAILOVER | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) Refer to procedure 2.5.2 for Actions When Frequency Telemetry is Incorrect. |

## 2.5.2	Actions When Frequency Telemetry is Incorrect

Procedure Purpose: To prevent the unnecessary deployment of Responsive Reserve due to incorrect telemetry frequency data.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-005 R8 |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| 1 | IF frequency is BELIEVED to be incorrect VERIFY that the frequency is correct by comparing the data from multiple sources. - Go to the “Generation Area Status” display, and click on the “i” to the left of “Current Frequency” to view “OPA Measurement” window. |
| 2 | In “OPA Measurement” window, under “Status” column, check “Prime” on a valid frequency source. |
| 3 | Refer to section 2.5.1 for action to be taken to correct frequency. |
| 4 | LOG in the Operator’s Log any relevant information on this event. |

## 2.5.3	Monitor and Control Time Error Correction

Procedure Purpose: This procedure will establish the standard for implementing time error correction.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 2.2.7 |  |  |  |
| NERC Std. | BAL-004 |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT ISO is the Reliability Coordinator and Balancing Authority that implements and terminates ERCOT Time Corrections in accordance with ERCOT Protocols and Operating Guides. ERCOT Reliability Coordinator is the Interconnection Time Monitor within the ERCOT Interconnection. |
| REQUIREMENTS: | When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. Time error corrections normally start and end on the hour or half-hour. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction. However, at no time should the accumulated time error be allowed to exceed five (5) seconds. Time error correction notifications shall be labeled alphabetically on a monthly basis (A-Z). In the succeeding month, the first time error correction will revert back to “A”. |
| 1 | DISPLAY the Generation Area Status display. Reference Display: Generation Area Status – Time Error – “Correction Schedule” |
| 2 | Select Time Error – Correction Schedule. |
| 3 | ENTER the appropriate Time error ID letter. |
| 4 | ENTER the frequency offset using – 0.02 for fast time correction (59.98 Hz) or +0.02 for slow time correction (60.02 Hz). |
| 5 | ENTER a Start Time later than the current time AND ENTER a Stop Time later than the scheduled start time. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 6 | Notify all QSEs using a hotline call, if available, before starting time correction, of the start time and frequency offset. Typical script: “This is ERCOT operator [first and last name]. ERCOT is initiating a time error correction, we will ENTER the frequency offset using [– 0.02] or [+0.02] at [time]. The current time error is [time]. Thank you.” Review Hotline participants and log any issues. If necessary call participants individually. |
| 7 | VERIFY the Manual radio button to be selected. Time correction will start at selected date and time. Reference Display: Generation Area Status – “Time Error” – Correction Schedule |
| 8 | Monitor the time error on the Generation Area Status Display until it reaches an acceptable value (+/- 0.5 seconds). Time error correction may be terminated after five hours, or after any hour it has reached an acceptable value of +/- 0.5 seconds. |
| 9 | If a time error correction is prematurely terminated, wait at least one hour between sending the termination and re-initiation notices. |
| NOTE: | The following notice is to allow QSEs time to incorporate the changed frequency in their Ancillary Service Performance Monitor. |
| 10 | - Notify all QSEs using a hotline call, if available, before ending time correction. Typical script: “This is ERCOT operator [first and last name]. ERCOT is ending the time error correction at [time]. The current time error is [time]. Thank you.” - Review Hotline participants and log any issues. If necessary call participants individually. |
| 11 | LOG in the Operator’s Log start time, stop time, Time error ID letter, time error, and frequency offset for each start and termination. |

2.5.4 	Potential DCS Event

Procedure Purpose: To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002 R2.4, R6.2 | EOP-001 R5 | EOP-002 R5, 6.1 |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | There are times when the MW amount lost will be more than the NERC reportable amount. In these cases LaaRs can be used to recover frequency. |
| NOTE: | NERC Recovery Criteria Within 15 minutes ERCOT shall: - Return system frequency to scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Return system frequency to its pre-disturbance value if it is was less than scheduled frequency prior the disturbance. ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s largest single contingency (1354 MW) as soon as practical. Within 90 minutes, ERCOT ISO will restore Responsive Reserves to 2300 MW or greater. This 90 minute restoration period begins at the end of the disturbance recovery period. A potential NERC Reportable DCS Event - Single contingencies – one event characterized by the sudden, unanticipated loss of generation greater than or equal to 1083 MW OR - Multiple contingencies – the loss of multiple units within one minute or less if the combined magnitude exceeds 1083 MW. It is anticipated that the deployment of LaaRs will occur in stages. LaaRs UFRs are set at 59.7 Hz. If ERCOT declares an “Emergency Notice”, a text message may be sent as time permits so as not to impede system operations. In order to control frequency, be prepared to issue a “Fleet Down” VDI once the system has recovered to its scheduled/pre-disturbance frequency value. |
| 1 | When a low frequency disturbance occurs due to a loss of generation, DETERMINE immediately, by calculating the loss of generation, if the event is potentially a NERC Reportable DCS Event. |
| 2 | If a low frequency disturbance occurs, AND there is NO indication of a generation loss, determine the magnitude of the event by using the “Interconnection Control Error ” tag, Analyze the change in this tag after a minimum of 20 seconds to avoid the initial overshoot. Assume that a potential DCS event has occurred and SCADA communications has been lost if the total generation loss is greater than 1000 MW, implement Step 4 of this procedure. - Determine the magnitude of the event by using the “Interconnection Control Error” tag on the “ERCOT & QSE Summary Page” in PI. - Take care to calculate the entire generation loss from the PI tag, not just the difference between zero and the lowest number. Example: If the “Interconnection Control Error” pre-disturbance value is +150 MW, and post disturbance value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. |
| 3 | IF the event is not a NERC Reportable DCS Event, proceed with normal operation. |
| 4 | IF the event is a potentially NERC Reportable DCS Event and the Frequency is above 59.7 Hz, - When system conditions warrant, issue a VDI using the hotline instructing QSEs to deploy ALL un-deployed LaaRs and hydro generation that are bid to supply Responsive Reserve. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing Verbal Dispatch Instruction F-(mmddyy-#) to all QSEs and instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Verbal Dispatch Instruction instructing all QSEs to deploy LaaRs and hydro supplying Responsive Reserve. [QSE] please repeat this directive back to me. That is correct; I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 5 | Review Hotline participants and log any issues. If necessary call participants individually. |
| 6 | Complete the VDI form (See Desk Top Guide Section 7.4) and process. - Issued a Verbal Dispatch Instruction to – write in “All QSEs” - Receiving entity’s operator – write in “All QSEs” - The instruction was as follows: “All QSEs are required to deploy any un-deployed LaaRs and hydro supplying Responsive Reserve due to a potential DCS event.” |
| 7 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being deployed. |
| NOTE: | verify all RRS from resources is recalled prior to restoring LaaRs providing RRS. |
| 8 | REQUEST that the Transmission & Security Desk notify the Transmission Operators that LaaRs are being restored. |

## 2.5.5 	LaaR Deployment for North-Houston Voltage Stability Limit

Procedure Purpose: To maintain North-Houston voltage stability.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001 R2, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.7, R3 | IRO-006-3 R1 |
|  | TOP-002-2 R10 |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | Deploy LaaRs in the Houston zone that are bid into the Responsive Reserve market when requested by the Transmission and Security Desk for the North – Houston IROL. - Make Hotline call to deploy LaaRs in the Houston zone that are bid into the Responsive Reserve market. - Post a message on the MIS: Typical Script: This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is instructing QSE’s to deploy LaaRs located in the Houston Zone that are bid into the market within ten (10) minutes. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | Review Hotline participants and log any issues. If necessary call participants individually. |

## 2.5.6	 Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-003-2 R2 | IRO-005-1 R1.1 |  |  |

| Approved by: |  |  | Effective Date: March 9, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: Page 1: 345 KV Transmission Equipment Status Page 2: 138 KV Transmission Equipment Status Page 3: Generator Breaker Status Page 4: Transmission Line Overloads and Voltage Violations- critical alarms Page 5: Generator Unit, QSE SCE, and ERCOT ACE Status Page 6: RTNET Status Page 7: ICCP Status Page 8: EMS Task Application Alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 5, 6, and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Transmission & Security Desk to clear the alarms approximately every 2 to 3 hours or as needed. |

## 2.6.10	 Loss of Primary Control Center Functionality

Procedure Purpose: This procedure is to be performed by the Operator at the alternate Control Center (ACC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost OR

- As directed by the Shift Supervisor.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001 R5 | EOP-001 R4.4 | EOP-008-0 | IRO-005 R1.10 |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 9 |  |

| Step | Action |
| --- | --- |
| Contact Security | IF: - You are unable to reach any Operators at the PCC (cell phone or PBX Bypass phones), THEN: - Check the Control Room video camera to determine the status of the PCC and personnel. - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired. |
| Constant Frequency | Place a large QSE (that has regulation reserve) on constant frequency, by issuing a VDI. * * * WARNING * * * When placing a QSE on constant frequency control, place ERCOT AGC in Monitor mode. |
| Notify Market Participants | Place the following Hotline calls to the QSE’s and TO’s: Hotline call to QSEs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT is declaring an emergency and is transferring operations to the alternate control center. Until further notice, direct all urgent phone calls to (512) 225-7100. ERCOT has put a QSE on constant frequency. All remaining QSEs follow your base power schedules and hold interval ending [last interval]. VDI # is [#]. Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat this directive back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call to TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; ERCOT declaring an emergency and is transferring operations to the alternate control center. Until further notice, direct all urgent phone calls to (512) 225-7100. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report zonal CSC transfers, West - North and North – Houston stability limits if power flows reach 90% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any abnormal line operations.” [Select TO], “Please repeat this directive back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Notify the appropriate Nuclear Plant’s QSEs and inform them that ERCOT’s RTCA is not function and is expected to be functional within [# minutes]. |
| Call in Additional Operators | IF: - The shift personnel at the PCC will NOT be relocating, THEN: - Call in additional shift personnel, which include a Shift Supervisor, via the Communicator! NXT Notification System (NXT). Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Notify the following: - Manager of System Operations and/or designee - If unable to reach Manager of System Operations and/or designee, notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers have been programmed into the control room cell phone. |
| Monitor Critical Facilities | Potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the ERCOT website under ‘Grid Information’ in the Transmission section http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA)” in the key document section. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble keeping up, THEN: - Issue fleet VDIs to other QSEs to help out OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). OR IF: - QSEs call in with questions about the Day-Ahead Market, THEN: - Notify the QSE that the Day-Ahead Market functions will resume when additional staff reports to work. - Document which QSEs call in and the questions they have to pass along to the Day-Ahead Operator when he/she reports to work. |
| Respond to TSPs | IF: - TOs call in to report the following: - Thermal limits have reached their continuous rating, - Zonal CSC transfers have reached 90% of the last posted limit, - West-North stability limit has reached 90% of its limit,, - North-Houston stability limit has reached 90% of its limit, THEN: - If EMS is available, verify their values against ERCOT’s, - Take immediate action, as listed below, for thermal limits and stability limits, - Continue to monitor the zonal transfers; Instruct the TO to do the same and notify ERCOT should the limits reach 95%, - Prepare to respond, as listed below, should the zonal transfers reach 95% and trending upward. |
| Stability Limits Reached 90% (IROL) | IF: - The West-North stability limit is approaching 90% and is continuing to trend upward, - The North-Houston stability limit is approaching 90% and is continuing to trend upward, - Notified by TO that a stability limit is approaching 90% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west, - Issue VDIs as necessary to relieve the congestion, - If VDIs are issued, monitor QSE on constant frequency |
| Thermal Limits Reached and Zonal Transfers at 95% (SOL) | IF: - Thermal limits have reached their continuous rating and are continuing to trend upward, OR - Zonal transfers have reached 95% of their limit, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - When you decide the recommended actions are valid, implement the plan and issue VDIs as necessary. - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Operator Technical Logs | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution Time of system or function restoration |

## 2.7.1	Approve E-Tags for SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005 R1 | INT-006 R1, R1.1, R1.2, R1.3, R1.2 | INT-007 R1.1, R1.2 | INT-009 R1 |
|  | TOP-002-2 R5, R9 |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Columbus, Ohio is the Tie Operator for the East and North DC Ties. The designation in WebTrans for the East tie is DC_E and the North tie is DC_N. |
| NOTE: | Do not approve an E-Tag that crosses the midnight hour. We need one E-Tag per day in order for the schedules to transfer into the Market system correctly. |
| NOTE: | Each time a new or updated E-Tag is submitted, the WebTrans system will automatically validate the E-Tag. WebTrans will display whether the E-Tag has passed or failed validation. The criteria ERCOT uses to validate E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated E-Tag. - TP Required-ERCOT must be specified as a Transmission Provider in the Physical Path of the E-Tag. Currently the validation criterion set to automatically deny an E-Tag is “QSE Contract” and “TP Required”. If either or both of these validations fail the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/docs/QSEs.xls Select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Monitor |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: 1.1 Determine if the following information is correct on the E-Tag: - Ensure “ERCO” is not listed as a PSE in the Physical Path - “ERCOT-E” or “ERCOT-N” is selected for the correct Point-of-Receipt (POR) or Point of Delivery (POD) portion of the physical path. - “CSWS” is included as a Scheduling Entity on the SWPP TP row in the physical path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the physical path. (Note: If CSWS is listed in both the Scheduled Entities column and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied). - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on a quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. 1.2 If one or more E-Tags are submitted that will cause the DC Tie to be overscheduled: - Contact SPP to ensure they also see the over-schedule and they will ensure the appropriate actions are taken to correct the over-schedule. Also inform SPP that if the appropriate actions to correct the over-schedule are not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. - IF an E-Tag is curtailed to zero (0) due to an over-schedule that was not corrected in time, contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. 1.3 Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag is automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag is not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Monitor Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve an E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the E-Tag approval timeline, the E-Tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag data to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |

## 2.7.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005 R1 | INT-006 R1, R1.1, R1.2, R1.3, R1.2 | INT-007 R1.1, R1.2 | INT-009 R1 |
|  | TOP-002-2 R5, R9 |  |  |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | Do not approve an E-Tag that crosses the midnight hour. We need one E-Tag per day in order for the schedules to transfer into the Market system correctly. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE; this will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export) |
| NOTE: | The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-tags are scheduled. |
| NOTE: | Each time a new or updated E-Tag is submitted, the WebTrans system will automatically validate the E-Tag. WebTrans will display whether the E-Tag has passed or failed validation. The criteria ERCOT uses to validate E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated E-Tag. - TP Required-ERCOT must be specified as a Transmission Provider in the Physical Path of the E-Tag. Currently the validation criterion set to automatically deny an E-Tag is “QSE Contract” and “TP Required”. If either or both these validations fail the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/docs/QSEs.xls Select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Monitor Summary |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: - Determine if the following information is correct on the E-Tag: - Ensure “ERCO” is not listed as a PSE in the Physical Path - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. - Determine if one or more E-Tags being submitted will cause the DC Tie to exceed the import/export limit for the tie. If E-Tags are received in Day-Ahead then no import/export limits will have been posted yet, proceed to step 1.3 - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the import/export limit for the tie. - Call the PSE to have the E-tag modified, if modification is not done 20 minutes before the start of the ramp then; - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. - Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag is automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag is not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Monitor Tag Validation Criteria Tag Approval Monitor - QSE Summary |
| 2 | The ramp rate for the Railroad DC-Tie will be 50 MW per minute due to reactive issues on the CFE side. Laredo and Eagle Pass DC-Ties will be ramped across a 10 minute window. - Ensure the ramp duration is filled out on Railroad E-Tags only - Laredo and Eagle Pass ramp duration will remain blank Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| 4 | ERCOT will allow QSE’s to submit E-Tags more than one (1) day in advance on the CFE DC-Ties. In these cases there will not be an associated schedule until the day-ahead. If a schedule is not received by 1400 in the day-ahead, notify the QSE and remind them that a schedule is needed. If the schedule is not received by 2000, curtail the E-Tag to zero. |
| 5 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

## 2.7.5	Curtailment of SPP DC Ties

Procedure Purpose: The process to curtail E-tags for the SPP DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005 R1.1 | INT-010 R1 | IRO-006 R5 |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 1 |  |

| Step | Action |
| --- | --- |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | When a curtailment alarm is received in WebTrans, - Approve the E-Tag curtailment. WebTrans Reference Displays: Tag Validation Monitor Tag Approval Monitor |
| 2 | If a QSE or SPP requests an E-Tag be curtailed or adjusted for any reason, curtail the E-Tag to 0 (zero). |
| NOTE: | E-Tag curtailments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI) |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each DC Tie affected by E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

## 2.7.7	Managing Daily Inadvertent Energy for the SPP DC Ties

Procedure Purpose: To do before-the-fact and after-the fact checkouts for the SPP DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-005 R12.1 | INT-003 R1.2 | INT-009 R1 |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when a E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ERCOT-E, ERCOT-N) or if ERCOT is left off the E-Tag as a Scheduling Entity (SE). |
| CAUTION: | CAUTION If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Ohio TO for the North and East DC Ties |
| NOTE: | Due to a deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW out of ERCOT and into SPP, OR - Add MW flow in the direction of the schedule |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 10 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, select “Schedule” on the “Checkout” dropdown on the Filtering Options button so the “SC” column appears. Check the bottom box in Column SC and click the “Apply Checkout” button. Proceed to Step 5. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the North and East DC Ties and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

## 2.7.8	Managing Daily Inadvertent Energy for the CFE DC Ties

Procedure Purpose: To do before-the-fact and after-the-fact checkouts for the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-005 R12.1 | INT-003 R1.2 | INT-009 R1 |  |

| Approved by: |  |  | Effective Date: March 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| OVERVIEW: | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE: | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the physical path (ROAD_DC, EGPS_DC, or LAR_VFT) or if ERCOT is left off the E-Tag as a Scheduling Entity (SE). |
| CAUTION: | CAUTION If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| NOTE: | When communicating with the DC Tie Operator: - Contact AEP Corpus Christi TSP for the Eagle Pass and Railroad DC Ties, and the Laredo VFT. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator. If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: QSE Summary BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less that 5 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, talk with the DC Tie Operator to check out the total scheduled and actual values for each DC Tie. If both parties agree on the Scheduled In and Out values and on the Actual In and Out values, select “Schedule” on the “Checkout” dropdown on the Filtering Options button so the “SC” column appears. Check the bottom box in Column C and click the “Apply Checkout” button. No further action is required. WebTrans Reference Display: ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to workout all discrepancies If the discrepancy is with the scheduled values: - Check the box for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change our value to match the DC Tie Operator’s value. Reference Displays: ATF Tie Data |
| 5 | Create an Excel file for each of the CFE DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |