## Power Operations Bulletin # 473

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1.1 	System Overview

Procedure Purpose: Analyze data to maintain system security.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-002-1 R6, R8 | IRO-005-2 R1.1, R1.2, R1.3 | NUC-001-1 | PRC-001-1 R2.2 |
|  | TOP-006-1 R2 |  |  |  |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision | 3 |  |

| Step | Action |
| --- | --- |
| REVIEW | REVIEW each of the following as necessary to confirm system reliability status - Alarms - State Estimator (SE) - Real Time Contingency Analysis (RTCA) - Real Time Constraint Analysis (RTCAM) - Approved and Forced Outages - Load Forecast - Daily Transmission Limits - Voltage and Stability Limits - Real Time Monitoring (RTMONI) - Real Time Balancing Market - Real Time Reserve Monitoring |
| GAP STUDY | At the start of each day (after midnight), run a gap study to ensure all contingencies can be solved. If necessary, request the Shift Engineer to review results and make suggestions. If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units. Make a log entry with your efforts. |
| STP LINES | A minimum of two transmission lines should be in service at all times. The in-service lines should be from at least two of the groups in the table below: Independent Groups of STP Transmission Lines Group 1; Group 2; Group 3. STPZWP39; STPELM18; DOWSTP18. STPELM27; DOWSTP27. STPWAP39. Note: Transmission lines Blessing, HLJSTP64, and CKT_3124 are not included in this table because these circuits are not part of STP’s credited offsite sources. If a minimum of two lines are not in service, notify the QSE. |
| PROTECTIVE RELAY OR EQUIPMENT FAILURE | When notified by a TSP that a protective relay or equipment failure reduces system reliability: - Ask the TSP how it reduces ERCOT Grid system reliability and if any corrective actions have been taken - Notify the Shift Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes. - Determine if other TSPs are affected by this failure and make notification by phone. - Make log entry of events |

## 2.2.1	Real Time Contingency Analysis (RTCA)

Procedure Purpose: To monitor SOLs and have situation awareness of the transmission system

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R4.2 | EOP-003-1 R6 | IRO-002-1 R6, R8 | IRO-003-2 R1 |
|  | IRO-004-1 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006-3 R1, R4 | TOP-001-1 R1, R2, R5 |
|  | TOP-002-2 R6, R8, R10 | TOP-004-2 R1, R6, R6.6 | TOP-006-1 R5 | TOP-008-1 R1, R2, R4 |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 6 |  |

| Step | Action |
| --- | --- |
| NOTE: | System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit violations. Following a separation from the Interconnection, and following automatic underfrequency load shedding, System Operators will also direct TSPs to shed additional load manually when there is insufficient generating capacity to restore system frequency. |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. Zonal Congestion Management Techniques are OC1s. Deployment of Non-Spin may be used if approved by the Shift Supervisor. Local Congestion Management Techniques consist of OC3s, unit specific dispatch instructions (OOME or VDIs), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Mitigation Plan (MP), and Temporary Outage Action Plans (TOAP). TOAP guidelines are located in the Outage Notes. Unit specific dispatch instructions may be determined by Shift Factors or studies, whichever the system operator deems most appropriate. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. |
| NOTE: | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Energy Management System (EMS) and an electronic copy is located on the ERCOT website under ‘Grid Information’ in the Transmission section. http://www.ercot.com/gridinfo/transmission/index Select “Operations Contingency List (ESCA) in the key document section. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| 1 | VERIFY RTNET and RTCA processes are enabled. If not, enable them. |
| 2 | Determine if RTCA has run within 10 minutes. |
| 3 | If RTCA has not run within 10 minutes, refer to Section 2.1.2, Analysis Tool Outages. |
| 4 | EXAMINE the RTCA contingency violations “Branch” summary, and ENSURE that no post contingency overloads greater than 100% of the emergency rating exist. IF post-contingency overloads greater than 100% of the Emergency Rating exist: - ENSURE that no Special Protection Scheme (SPS), Remedial Action Plan (RAP), Pre-Contingency Action Plan (PCAP), Temporary Outage Action Plan (TOAP), or Mitigation Plan (MP) exists to alleviate the loading post contingency, AND - ENSURE the Pre-contingency value listed on the violation summary is reasonably accurate. NOTE: The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at P:\Remedial Action Plans A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant. TOAPs are usually located in the daily Outage Notes. |
| 5 | EXAMINE the RTCA contingency violations “Voltage” summary (it has multiple pages), and ENSURE that no post contingency over voltage or under voltage violations outside of the range of the emergency switchyard voltage requirements exists at the STP and CPSES 345 kV buses. Comanche Peak Emergency Switchyard Voltage Requirements System; 345 kV; 138kV. Nominal Voltage; 352 kV; 141 kV. Tolerance; +2.56% or -3.40%; +2.13% or -4.26%. Maximum Voltage; 361 kV; 144. Minimum Voltage; 340 kV; 135. South Texas Project Emergency Switchyard Voltage Requirements System; 345 kV. Nominal Voltage; 362.25 kV. Tolerance; +0% or -6.14%. Maximum Voltage; 362.25 kV. Minimum Voltage; 340 kV. If post-contingency violations outside the range of the emergency switchyard voltage requirements exist, COORDINATE with the Transmission Operator and QSE and take appropriate voltage control action. When STP is in an alternate line up, the minimum voltage is 347kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is the STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 6 | IF the pre-contingency value appears to be accurate and a SPS, RAP, PCAP, TOAP, or MP exists, refer to the respective procedure and operate accordingly. |
| 7 | IF the SCADA is of similar magnitude to the Pre-contingency value and no SPS, RAP, PCAP, TOAP, or MP exist, go to step 8. |
| NOTE: | When making any changes to the SCADA database, document the changes using the SCADA tagging function. Refer to Desk Top Guide Section 3.6 for guidance. |
| 8 | IF the Pre-contingency value appears to be inaccurate, do NOT employ congestion management techniques. - Inform the Shift Supervisor and he/she will decide if an Operations Support Engineer should be called. |
| 9 | IF post contingency overloads greater than 100% exist without an SPS, RAP, PCAP, or a TOAP is in place to relieve, EMPLOY congestion management techniques to eliminate the post contingency overloading. |
| 10 | IF post contingency overloads greater than 100% of the “15-minute Rating” exist with a RAP in place to relieve, EMPLOY congestion management techniques to reduce the predicted post contingency loading to no more than 100% of the 15-minute rating. |
| 11 | IF any RTCA results predict a Facility Rating will exceed post-contingency loading 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL. Proceed to section 2.2.3 Potential IROL’s. |
| 12 | If congestion management techniques fail to resolve congestion and no practicable resource solution exists, ISSUE a Watch per section 2.5.3. |
| 13 | Periodically check the Base Case violations display for Thermal overloads. A “thermal overload in real-time” means loading above 100 % of the NORM/Continuous rating. |
| 14 | If a valid Thermal overload exists in real-time, EMPLOY congestion management techniques to relieve the overload. If the system operator determines that the Pre-contingency value or system topology is incorrect, step 13 may be omitted. |
| 15 | Periodically check the “Contingency Solution Results” display. If there are unsolved contingencies, run the State Estimator again. If unsolved contingencies remain, call the on-call State Estimator Support Engineer. If any unsolved (pink) contingencies exist for an extended period of time, as time permits, notify the on-call Operations Support Engineer. If there are known reasons that the contingency is unsolved, as time permits, notify the on-call Operations Support Engineer to verify system conditions have not changed. |

## 2.2.11	SPS Monitoring

Procedure Purpose: To monitor SPS’s.

| Protocol Ref. | 6.5.11 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 7.2.2 |  |  |  |
| NERC Std. | EOP-001-0 R4.2 | IRO-002-1 R8 | IRO-005-2 R1.1, R1.3, R12, R16, R17 | PRC-001-1 R6 |
|  | TOP-006-1 R3, R5 |  |  |  |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 7 |  |

| Step | Action |
| --- | --- |
| NOTE: | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE: | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingent loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario congestion management is not needed until the criterion in Desk Top Guide Section 3.4 is met. |
| 1 | Special Protection Schemes (SPS) - EXAMINE the results in RTCA for SPS activation. - If “SPS” is identified as a post contingent overload, EXAMINE the color of the background. - Refer to Desk Top Guide Section 3.4 for actions to be taken based on the color of the background. |
| NOTE: | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at P:\Remedial Action Plans |
| NOTE: | Typically SPS’s are to solve post-contingent overloads on the Transmission System. Due to outages, either (Planned or Forced) the Transmission topology is changed temporarily. During these conditions the ERCOT Transmission & Security operator(s) will utilize Congestion Management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | Monitor the Excel spreadsheet “Real Time Values” - Each SPS will be displayed, as the SPS activation threshold increases the display changes colors - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 3 | For system reliability, it may be necessary to prevent an SPS from activating. |
| SPS Operation | If an SPS operates (generation disconnects from the system): - Notify Shift Supervisor of the need for a Texas RE Report - Refer to 2.1.3 OOME – VDI Guidelines, if requested by QSE |
| SPS Runback | If an SPS arms or activates (runs back): - Issue OOME instruction if it appears the SPS will run back again if reset. - Notify the TSP to reset SPS. |
| SPS STATUS CHANGE | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated. - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” - Post message on MIS to make TO notification. Typical message: The [name] SPS has been [placed in or taken out of] service. |

## 2.4.2 	Assist Transmission Operator with Voltage Issues at Nuclear Power Plants

Procedure Purpose: Maintain actable voltage levels at nuclear power plants.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 | TOP-002-2 R8 |  |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT and TSPs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| 1 | WHEN notified by a Transmission Operator of an issue with the switchyard voltage at the South Texas Project or Comanche Peak, ENSURE voltage remains within the following limits: For Comanche Peak ###### System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144. - Minimum Voltage; - 340 kV; - 135. For South Texas Project ###### System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or - -6.14%. - Maximum Voltage; - 362.25kV. - Minimum Voltage; - 340kV. When STP is in an alternate line up, the minimum voltage is 347kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 2 | IF voltage exceeds maximum or minimum THEN COORDINATE with the Transmission Operator and QSE and DIRECT appropriate voltage control action. |
| 3 | Once voltage is back to normal range, notify the appropriate Nuclear Plant’s QSE and inform them. |
| NOTE: | Calaveras (Spruce, Von Rosenberg, etc), DOW, WAP, are points at which generation voltage adjustments can be expected to impact control of STP voltage. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. |

## 2.4.4 	Power System Stabilizers (PSS) and Automatic Voltage Regulators (AVR)

Procedure Purpose: To ensure that power system stabilizers and automatic voltage regulators stay “in service” whenever possible.

| Protocol Ref. | 6.5.7.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. | 2.2.4 |  |  |  |
| NERC Std. | IRO-002-1 R8 | IRO-005-2 R1.1, R1.3 | VAR-001-1 R6, R6.1 | VAR-002 R3.1 |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 6 |  |

| Step | Action |
| --- | --- |
| NOTE: | QSE’s will inform ERCOT of a change in status with any PSS or AVR by phone. |
| 1 | The ERCOT Operator will: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service - Ensure that the QSE has notified the TO of the change in status - Enter the status change information into the ERCOT Logs - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability.xls” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| NOTE: | Operations Planning will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT Sharepoint > Operations Support > AVR AND PSS Status |

## 2.6.6	 Monthly Testing of Satellite Phone System

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-001-1 R2 | EOP-005-1 R5 |  |  |

| Approved by: |  |  | Effective Date: March 31, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
|  | Primary Control Center |
| NOTE: | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE: | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers. As the Shift Supervisor makes the calls to the individual Transmission Service Provider, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate Transmission Service Providers. |
| NOTE: | Use the ERCOT Satellite Phone User Guide located in Section 7 of the Desktop Guide for a list of the Transmission Service Providers that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge Call. |
| 1 | - On page 11 of the MX Turret phone select the appropriate line that applies to the ERCOT Operations Desk that is making the call. These numbers are located in the bottom right of the page 11 screen. BKST Day- Day Ahead Desk BKST Freq.- Frequency Desk BKST OPD – Operating Period Desk BKST TS #1 – Transmission Desk #1 BKST TS#2 – Transmission Desk #2 - If the preprogrammed number does not function correctly, refer to Section 7 of the Desktop Guide for the appropriate conference number. - When prompted enter the Moderator Pass Code. - If necessary wait on the line for approx. five minutes for the Participants to dial into the Conference Bridge. - As each participant connects to the Conference Bridge record the name of the individual from the Transmission Service Provider making the call and any problems identified with the connection process. |
| 2 | - If one or more of the Transmission Service Providers fails to connect to the Satellite Phone System Conference Bridge Call investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the Transmission Service Providers not able to connect in the initial test. |
| 3 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| 4 | Log the test results in the Operations Log. |
|  | Alternate Control Center |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| 3 | Log the test results in the Operations Log. |