## Power Operations Bulletin # 487

ERCOT has revised the Frequency Control Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1.2	Three Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: August 30, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| 3 | Our standard expectation is that three-part communication will be used for all but face-to-face communication and will be used for all communications regardless of whether or not they are directives. |

## 2.5.1	Frequency Control Operating Procedure

Procedure Purpose: To maintain system frequency within acceptable levels.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | BAL-002-0 R6, R7, R8 | BAL-005-0.1b R6 | BAL-007 | NUC-001 |

| Approved by: |  |  | Effective Date: August 30, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 7 |  |

| Step | Action |
| --- | --- |
| Objective: | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 Reference Displays: Generation Area Status Responsive, Regulation, and SCE – Regulation Responsive, Regulation, and SCE – Regulation – Details |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency id greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 600 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -600 MW |
| Response to High Frequency |  |
| BAAL SHEET | Open realtime on ‘erpfileb’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| MONITOR/ FLEET | Frequency above 60.05 (Hz) and continuing to climb or over 60.05 (Hz) > five minutes: - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. - If out of Down Regulation, issue fleet down instruction to a QSE with positive SCE (see script below). |
| 10 MINUTES | If 10 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - If out of Down Regulation, issue additional fleet down instructions to the QSE(s) with positive SCE. Issue Verbal Dispatch instructions to one or more QSE’s with positive SCE: Typical script: This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#] to [QSE]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. Reduce your fleet generation by [MW amount] due to high frequency. Please repeat this back to me. That is correct. I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 15 MINUTES | If 15 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Issue fleet down instructions to QSEs with Down Regulation room (see script above). - Log the event and notify Shift Engineer. - Shift Engineer will send the event notification via email to BAALfieldtrials@ercot.com |
| 20 MINUTES | If 20 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Remove SCE feedback from QSEs with positive SCE and monitor frequency response. - Issue fleet down instructions to additional QSE(s) with positive SCE. - Issue fleet down instructions to additional QSEs with Down Regulation room (see script above). - Log the event and actions undertaken to bring the frequency below BAAL trigger limit. |
| 25 MINUTES | If 25 consecutive minutes of ACE above BAALHigh (60.09 Hz): - Issue fleet down instructions to additional QSEs with Down Regulation room (see script above). - Log the event and actions undertaken to bring the frequency below BAAL trigger limit. |
| STABLE | Once regulation is restored and frequency is stable, end fleet down generation instructions: Typical script: This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time]. This ends the fleet down instruction. Please repeat this back to me. That is correct, thank you.” |
| Response to Low Frequency |  |
| BAAL SHEET | Open realtime on ‘erpfileb’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| MONITOR / DEPLOY | Frequency below 59.95 (Hz) and continuing to drop or below 59.95 (Hz) > 5 minutes: - Remove SCE feedback from QSEs with negative SCE and monitor frequency response. - Consult with the Transmission and Security desk to confirm that no OOMs from that desk could be affecting frequency. - If out of Up Regulation, change the “Deploy Freq (Hz)” to 59.950 and “Recall Freq (Hz)” to 59.999. |
| 10 MINUTES | If 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with negative SCE and monitor frequency response. - Call QSEs with negative SCE and instruct them to increase generation to return their SCE to zero as soon as possible. |
| 15 MINUTES | If 15 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are being sent out. - Remove SCE feedback from QSEs with negative SCE. - Explain to the QSE with the negative SCE that their dispatch is causing the low Frequency with resulting frequency to be lower than NERC BAALLow trigger limit. Instruct the QSE with the negative SCE to bring their SCE back to zero within 10 minutes. - Log the event and notify Shift Engineer. - Shift Engineer will send the event notification via email to BAALfieldtrials@ercot.com. |
| 20 MINUTES | If 20 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - Monitor regulation services and ensure that deployments are sent out. - Remove SCE feedback from QSEs with negative SCE. - Explain to the QSE with the negative SCE that their dispatch is causing the low Frequency with resulting frequency to be lower than NERC BAALLow trigger limit. Instruct the QSE with the negative SCE to bring their SCE back to zero within 5 minutes. Get an update on dispatcher actions and corrective actions being taken. - Log the event and actions undertaken to bring the frequency above BAAL trigger limit. |
| 25 MINUTES | If 25 consecutive minutes of ACE is less than BAALLow (59.91 Hz): - If the non-compliant QSE’s inform you that they cannot restore zero (0) SCE or no QSE appears to be hanging out or no physical regulation down service is available. - Issue fleet up instruct to QSE(s) with Up Regulation room (see script). - Log the event and actions undertaken to bring the frequency above BAAL trigger limit. |
| VDI Script | Issue Verbal Dispatch instructions to one or more QSE’s (other than those failing to maintain SCE) to increase generation. Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing VDI [#] to [QSE]. Increase your fleet generation by [MW amount] due to low frequency. Please repeat this directive back to me. That is correct, thank you.” It is not mandatory that a VDI # is given with the directive, if filling out paperwork later, use script below: Typical script: This is ERCOT operator [first and last name]. Increase your fleet generation by [MW amount] due to low frequency. Please repeat this back to me. That is correct; I will call back with a VDI #.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| STABLE | Once regulation is restored and frequency is stable: Change the “Deploy Freq (Hz)” to 59.910 and “Recall Freq (Hz)” to 59.970 and end fleet up generation instruction. Typical script: This is ERCOT operator [first and last name]. ERCOT is ending VDI [#] at [time] This ends the fleet up instruction. Please repeat this back to me. That is correct, thank you.” |
| CRITERIA | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes. - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes. - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes. Individual performance will be assessed Level 0 if ACE exceeds the BAAL for more than 30 consecutive clock-minutes. |
| NOTIFY | If it is recognized that frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| Loss of Frequency Control |  |
| EMS ISSUES | IF the Energy Management System (EMS) frequency control is not functioning as indicated by: - AGC is SUSPENDED or PAUSED or - “Last AGC Cycle” time on Generation Area Status display is not updating, or - AGC operation adversely impacts the reliability of the Interconnection Place a large QSE (that has regulation reserve) on constant frequency, by issuing a VDI. |
| MONITOR MODE | - In the scenario where AGC operation adversely impacts the reliability of the interconnection, (ERCOT is handing over the frequency control to a large QSE), ERCOT AGC should be placed into the MONITOR mode. |
| QSE HOTLINE | Using the Hotline, notify all QSEs that ERCOT is having computer issues and is putting a QSE on constant frequency. - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is currently having computer issues and has put a QSE on constant frequency until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| TO HOTLINE | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| FLEET | If the QSE that is put on constant frequency is having trouble keeping up, issue fleet VDI’s to other QSE’s to help out or put a different QSE on constant frequency. Remember to take the first QSE off constant frequency. |
| QSE HOTLINE | When frequency control is functional, remove QSE from constant frequency. Notify all QSE’s by Hotline that ERCOT is back on control. - When QSEs have answered the Hotline, review Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is back to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” |
| TO HOTLINE | Notify the Transmission & Security Desk to make the same hotline call to the TO’s. |
| LOSS OF EMS OR SITE FAILOVER | The ability to view an adequate Frequency source during a site-failover, Database load or if AGC is temporarily unavailable may be limited. To view the system Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) Refer to procedure 2.5.2 for Actions When Frequency Telemetry is Incorrect. |

## 2.7.1	Approve E-Tags for SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005-2 R1 | INT-006-2 R1, R1.1, R1.1.2, R1.2, R1.3, R1.2 | INT-007-1 R1.1, R1.2 | INT-009-1 R1 |
|  | TOP-002-2 R5, R9 |  |  |  |

| Approved by: |  |  | Effective Date: July 1, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 6 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Columbus, Ohio is the Tie Operator for the East and North DC Ties. The designation in WebTrans for the East tie is DC_E and the North tie is DC_N. |
| NOTE: | Do not approve an E-Tag that crosses the midnight hour. We need one E-Tag per day in order for the schedules to transfer into the Market system correctly. |
| NOTE: | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| NOTE: | Each time a new or updated E-Tag is submitted, the WebTrans system will automatically validate the E-Tag. WebTrans will display whether the E-Tag has passed or failed validation. The criteria ERCOT uses to validate E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated E-Tag. - TP Required-ERCOT must be specified as a Transmission Provider in the Physical Path of the E-Tag. Currently the validation criterion set to automatically deny an E-Tag is “QSE Contract” and “TP Required”. If either or both of these validations fail the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform Operations Support. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Monitor |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: 1.1 Determine if the following information is correct on the E-Tag: - Ensure “ERCO” is not listed as a PSE in the Physical Path - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” is selected for the correct Point-of-Receipt (POR) or Point of Delivery (POD) portion of the physical path. - “CSWS” is included as a Scheduling Entity on the SWPP TP row in the physical path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the physical path. (Note: If CSWS is listed in both the Scheduled Entities column and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied). - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on a quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. 1.2 If one or more E-Tags are submitted that will cause the DC Tie to be overscheduled: - Contact SPP to ensure they also see the over-schedule and they will ensure the appropriate actions are taken to correct the over-schedule. Also inform SPP that if the appropriate actions to correct the over-schedule are not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. - IF an E-Tag is curtailed to zero (0) due to an over-schedule that was not corrected in time, contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. 1.3 Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag is automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag is not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Monitor Tag Validation Criteria Tag Approval Monitor QSE Summary |
| CAUTION: | Do not approve an E-Tag without an associated MOI schedule. If the QSE does not submit an MOI schedule before the end of the E-Tag approval timeline, the E-Tag will automatically be passively denied. |
| 2 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag data to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Display: QSE Summary Tag Approval Monitor |

## 2.7.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy, and should be in agreement with the Market Operating System (MOS) except for changes made during the Operating Period such as curtailments.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005-2 R1 | INT-006-3 R1, R1.1, R1.1.2, R1.2, R1.3, R1.2 | INT-007-1 R1.1, R1.2 | INT-009-1 R1 |
|  | TOP-002-2 R5, R9 |  |  |  |

| Approved by: |  |  | Effective Date: July 1, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 7 |  |

| Step | Action |
| --- | --- |
| NOTE: | AEP TO in Corpus Christi is the DC Tie Operator for the Railroad, Eagle Pass DC- Ties and the Laredo VFT. The acronym for the Railroad tie is DC_R, the Eagle Pass tie is DC_S and the Laredo VFT is DC_L. All communications will be with the DC-Tie Operator. The DC-Tie Operator will communicate with CFE. |
| NOTE: | Do not approve an E-Tag that crosses the midnight hour. We need one E-Tag per day in order for the schedules to transfer into the Market system correctly. |
| NOTE: | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE; this will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export) |
| NOTE: | The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-tags are scheduled. |
| NOTE: | Each time a new or updated E-Tag is submitted, the WebTrans system will automatically validate the E-Tag. WebTrans will display whether the E-Tag has passed or failed validation. The criteria ERCOT uses to validate E-Tags is: - QSE Contract-A QSE ID must be entered into the ERCOT Market Information field of the E-Tag. - QSE MW-A QSE’s MOI schedule must be greater than or equal to the associated E-Tag. - TP Required-ERCOT must be specified as a Transmission Provider in the Physical Path of the E-Tag. Currently the validation criterion set to automatically deny an E-Tag is “QSE Contract” and “TP Required”. If either or both these validations fail the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform Operations Support. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Monitor Summary |
| 1 | When a new or updated E-Tag is received in the OATI WebTrans system: - Determine if the following information is correct on the E-Tag: - Ensure “ERCO” is not listed as a PSE in the Physical Path - “Transaction type” must be “Energy or Normal” - AEPT is included as a Transmission Provider (TP) in the physical path and ERCO as a Scheduling Entity on the AEPT TP row in the physical path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start/Stop times for a new E-Tag must be on the quarter hour (:00, :15, :30, :45). If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. - Determine if one or more E-Tags being submitted will cause the DC Tie to exceed the import/export limit for the tie. If E-Tags are received in Day-Ahead then no import/export limits will have been posted yet, proceed to step 1.3 - Call AEP TO in Corpus Christi to ensure they also see that the DC Tie has exceeded the import/export limit for the tie. - Call the PSE to have the E-tag modified, if modification is not done 20 minutes before the start of the ramp then; - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. - Determine if the E-Tag passed or failed validation. - If the E-Tag passes validation, go to Step 2. - If the E-Tag fails validation and the E-Tag is automatically denied (QSE Contract), no further action is required. - If the E-Tag fails validation and the E-Tag is not automatically denied (QSE MW), go to Step 2. WebTrans Reference Displays: Tag Validation Monitor Tag Validation Criteria Tag Approval Monitor - QSE Summary |
| 2 | The ramp rate for the Railroad DC-Tie will be 50 MW per minute due to reactive issues on the CFE side. Laredo and Eagle Pass DC-Ties will be ramped across a 10 minute window. - Ensure the ramp duration is filled out on Railroad E-Tags only - Laredo and Eagle Pass ramp duration will remain blank Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| 4 | ERCOT will allow QSE’s to submit E-Tags more than one (1) day in advance on the CFE DC-Ties. In these cases there will not be an associated schedule until the day-ahead. If a schedule is not received by 1400 in the day-ahead, notify the QSE and remind them that a schedule is needed. If the schedule is not received by 2000, curtail the E-Tag to zero. |
| 5 | Periodically refresh the QSE Summary display during the E-Tag approval timeline to determine if a QSE has submitted an MOI schedule. When an MOI schedule has been received, compare the E-Tag to the schedule: - If the E-Tag is greater than the MOI schedule per 15 minute interval, then the MOI schedule does not have enough generation to cover the E-Tag. The “Mismatched” value box will be red and the MW difference will be a negative amount. Deny the E-Tag. - If the E-Tag is less than the MOI schedule per 15 minute interval, which means there is enough generation scheduled, the “Mismatched” box will be yellow and the MW amount will be a positive amount. Approve the E-Tag. - If the E-Tag equals the MOI schedule per 15 minute interval, which means there is enough generation scheduled; the “Mismatched” box will be green with a value of “0”. Approve the E-Tag. WebTrans Reference Displays: QSE Summary Tag approval Monitor |

## 2.7.6	Adjustments/Curtailment for the CFE DC Ties

Procedure Purpose: The process to curtail E-tags for the CFE Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005-2 R1.1 | INT-010-1 R2 |  |  |

| Approved by: |  |  | Effective Date: August 30, 2009 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 2 |  |

| Step | Action |
| --- | --- |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. After receiving the import/export limits for next day, it may be necessary to have the PSE adjust E-tags and schedules. |
| NOTE: | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Adjustments are done by the PSE which requires all parties to approve. |
| 1 | If any of the DC-Ties trip, ERCOT will have the responsibility to curtail the E-tags. - Curtail the E-Tags - Instruct AEP Corpus to make notification to CFE to approve curtailments |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s) - Re-load curtailed E-Tag(s) - Instruct AEP Corpus to make notification to CFE to approve re-loads |
| 3 | Once the import/export limits are posted around 1700, ensure the DC Tie(s) are not overscheduled. If an over schedule is found: - Notify the PSE to adjust the E-Tag(s) using the Last-in-First-Out. If just one PSE is involved they may adjust their E-Tags as they wish. - Notify AEP Corpus with the E-Tag number(s) to approve the adjustment(s) - Instruct AEP Corpus to make notification to CFE to approve adjustment(s) |
| 4 | Due to ERCOT transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by the Transmission & Security desk that a curtailment is needed: - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed. - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Instruct AEP Corpus to make notification to CFE to approve curtailment(s) |
| 5 | ERCOT must declare an Emergency in order to cut E-Tags without notice. If an Emergency has been declared for a transmission issue and if notified by the Transmission & Security Desk that a curtailment is needed: - Contact AEP Corpus that curtailment(s) will be made and to ramp the appropriate DC-Tie to the needed MW level. - Curtail the appropriate E-tag(s) - Notify AEP Corpus with the E-Tag number that was curtailed - Instruct AEP Corpus to make notification to CFE to approve curtailment Typical script to AEP Corpus: This is ERCOT operator [first and last name]. ERCOT will be curtailing E-Tag(s) on the [DC-Tie name] DC-Tie. Please start ramping the Tie to [MW level], the E-Tag will be curtailed shortly. Please repeat this back to me. That is correct.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 6 | Due to CFE transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by AEP Corpus or the Transmission & Security Desk of CFE’s situation: - Identify if at least 20 – 30 minute notice can be given for curtailment of E-Tag(s), if notice can be given proceeded. If curtailments need to take place immediately, proceeded to Step 7. - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed. - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Instruct AEP Corpus to make notification to CFE to approve curtailment |
| 7 | If notified by AEP Corpus or the Transmission & Security Desk of CFE’s emergency situation: - Verify the appropriate DC-Tie is being ramped - Curtail the appropriate E-tag(s) - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Instruct AEP Corpus to make notification to CFE to approve curtailment |
| 8 | If CFE does curtail schedules for their transmission issues: - Once curtailment is received from OATI, approve AND - Notify AEP Corpus that they see the curtailment and will ramp the Tie |
| 9 | Once notified that transmission issues are resolved and E-tags can be re-loaded: - Re-load curtailed E-Tag(s) - Ensure AEP Corpus sees the re-loaded E-Tags, AND - Instruct AEP Corpus to make notification to CFE to approve re-loads |

## 2.7.11	Emergency Energy across the CFE DC Ties

Procedure Purpose: Steps to secure emergency energy across the CFE DC Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R1, R3.1, R7.2, R7.3 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | INT-010-1 R3 | IRO-005-2 R4 |

| Approved by: |  |  | Effective Date: August 30, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NOTE: | ERCOT must declare a Watch or an emergency and make the proper posting/hotline call when receiving emergency energy from CFE, whether it is for transmission issues or an EEA situation. If CFE requests the emergency energy, no emergency notification needs to be declared. |
| 1 | When ERCOT is in need of Emergency Energy: When notified by Hotline or ERCOT operator of the need for emergency energy for a transmission issue or EEA situation: - Curtail all export E-tags that will help alleviate the emergency (see procedure 2.7.6, step 5), - Stop any export inadvertent energy payback, - If there is import capacity room on any/all CFE DC-Tie(s), contact AEP Corpus and request that they contact CFE to see if emergency energy is available, - If emergency energy is available, procure whatever is available, determine the DC-Tie(s), MW amount, time and duration (if possible), - Request AEP Corpus to ramp the appropriate DC-Tie with the emergency energy - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Forward VDI(s) to Shift Supervisor (fax) as time permits |
| 2 | When CFE is in need of the Emergency Energy: The request will come from either the Transmission & Security Desk or AEP Corpus: - If there is export capacity room on the appropriate DC-Tie(s), coordinated with the Transmission & Security Desk to ensure it will not cause ERCOT transmission issues - With no issues, determine the DC-Tie(s), MW amount, time and duration (if possible) - Coordinate with Operating Period Desk - Issue AEP QSE a VDI for the emergency energy and to AEP Corpus if requested - Notify AEP Corpus to ramp DC-Tie(s) - Forward VDI(s) to Shift Supervisor (fax) as time permits |