## Power Operations Bulletin # 491

ERCOT has revised the Frequency Control Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.7.6	Adjustments/Curtailment for the CFE DC Ties

Procedure Purpose: The process to curtail E-tags for the CFE Ties.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | INT-005-2 R1.1 | INT-010-1 R2 |  |  |

| Approved by: |  |  | Effective Date: September 9, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 3 |  |

| Step | Action |
| --- | --- |
| NOTE: | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. The DC-Tie Operator will communicate with CFE. |
| NOTE: | Import/export limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. After receiving the import/export limits for next day, it may be necessary to have the PSE adjust E-tags and schedules. |
| NOTE: | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Adjustments are done by the PSE which requires all parties to approve. |
| NOTE: | Once the import/export limits are posted around 1700 for next day, ensure the DC Tie(s) are not overscheduled. If an over schedule is found: - Notify the PSE to adjust the E-Tag(s) using the Last-in-First-Out. If just one PSE is involved they may adjust their E-Tags as they wish. - Notify AEP Corpus with the E-Tag number(s) to approve the adjustment(s) Instruct AEP Corpus to make notification to CFE to approve adjustment(s) |
| DC-Tie Trips |  |
| 1 | If any of the DC-Ties trip, ERCOT will have the responsibility to curtail the E-tags. - Curtail the E-Tags - Instruct AEP Corpus to make notification to CFE to approve curtailments |
| 2 | IF: - The curtailed E-Tag(s) go passive deny because CFE did not approve the curtailment in the allotted time; THEN: - Curtail the tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the E-Tag(s) curtailed. |
| 3 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s) - Instruct AEP Corpus to make notification to CFE to approve re-loads. |
| 4 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the E-Tag(s) curtailed. |
| 5 | IF: - The adjusted E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Contact PSE to send adjustment(s) through again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the E-Tag(s) curtailed. |
| Transmission Issues Within ERCOT |  |
| 1 | Due to ERCOT transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by the Transmission & Security desk that a curtailment is needed: - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed, - Notify AEP Corpus with the E-Tag number(s) that is being curtailed, - Instruct AEP Corpus to make notification to CFE to approve curtailment(s). |
| 2 | IF: - The curtailed E-Tag(s) go passive deny because CFE did not approve the curtailment in the allotted time; THEN: - Curtail the E-Tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the tag(s) curtailed. |
| 3 | ERCOT must declare a Watch or an Emergency in order to cut E-Tags without notice. If a Watch or an Emergency has been declared for a transmission issue and if notified by the Transmission & Security Desk that a curtailment is needed: - Contact AEP Corpus that curtailment(s) will be made and to ramp the appropriate DC-Tie to the needed MW level, - Curtail the appropriate E-tag(s), - Notify AEP Corpus with the E-Tag number, - Instruct AEP Corpus to make notification to CFE to approve curtailment. Typical script to AEP Corpus: This is ERCOT operator [first and last name]. ERCOT will be curtailing E-Tag(s) on the [DC-Tie name] DC-Tie. Please start ramping the Tie to [MW level], the E-Tag will be curtailed shortly. Please repeat this back to me. That is correct.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | IF: - The curtailed E-Tag(s) go passive deny because CFE did not approve the curtailment in the allotted time; THEN: - Curtail the E-Tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the steps above as necessary to get the tag(s) curtailed. |
| 5 | Once notified that transmission issues are resolved and E-Tags can be re-loaded, if applicable: - Re-load curtailed E-Tag(s), - Ensure AEP Corpus sees the re-loaded E-Tags, AND - Instruct AEP Corpus to make notification to CFE to approve re-loads. Repeat the steps above as necessary to get the tag(s) re-load. |
| 6 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the E-Tag(s) curtailed. |
| Transmission Issues within CFE |  |
| 1 | Due to CFE transmission issues it may be necessary for ERCOT to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by AEP Corpus or the Transmission & Security Desk of CFE’s situation: - Identify if at least 20 – 30 minute notice can be given for curtailment of E-Tag(s), if notice can be given proceeded. - If curtailments need to take place immediately, proceeded to Step 3. - Curtail the appropriate E-tag(s), allowing enough time for CFE to approve; at least 20 – 30 minute notice is needed. - Notify AEP Corpus with the E-Tag number(s) that was curtailed - Instruct AEP Corpus to make notification to CFE to approve curtailment |
| 2 | IF: - The curtailed tag(s) go passive deny because CFE did not approve the curtailment in the allotted time; THEN: - Curtail the tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the tag(s) curtailed. |
| 3 | If notified by AEP Corpus or the Transmission & Security Desk of CFE’s emergency situation and the need to immediately curtail E-tags(s): - Curtail the appropriate E-tag(s) - Confirm with AEP Corpus the E-Tag number(s) that is being curtailed and ensure appropriate DC-Tie is being ramped, - Instruct AEP Corpus to make notification to CFE to approve curtailment. |
| 4 | IF: - The curtailed tag(s) go passive deny because CFE did not approve the curtailment in the allotted time; THEN: - Curtail the tag(s) again, - Instruct AEP Corpus to make notification to CFE again. Repeat the following steps as necessary to get the tag(s) curtailed. |
| - 5 | Once notified that transmission issues are resolved and E-tags can be re-loaded, if appropriate: - Re-load curtailed E-Tag(s), - Ensure AEP Corpus sees the re-loaded E-Tags, AND - Instruct AEP Corpus to make notification to CFE to approve re-loads. |