## Power Operations Bulletin # 497

ERCOT has revised the Transmission and Security Desk Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1.3	OOMC/OOME – VDI Guidelines

Procedure Purpose: To provide guidelines for OOMEs and VDIs.

| Protocol Ref. | 6.5.11 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 |  |  |  |
|  | R4.2 |  |  |  |

| Approved by: |  |  | Effective Date: September 22, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | The order of steps in this procedure is a recommendation. The system operator will determine the sequence of steps, or any additional actions necessary to ensure system security. Step 2 does not apply to wind units. |
| 1 | When an OOMC is used in the adjustment period, call the QSE and instruct them to call and confirm their shut down before their OOMC expires and resource goes off-line. |
| 2 | If an OOME Dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that resource), then: - The duration of the OOME Dispatch instruction should end at the next scheduled off-line time according to the Resource Plan, OR the end of the operating day, whichever is shortest. - If the QSE representing the resource expresses a need for that resource to be returned on-line, and there is no negative impact on system reliability, then re-tract the OOME instruction for the appropriate intervals. |
| 3 | When system conditions require one CT of a Combined Cycle Plant to be OOME’d off line, use the following steps: - Contact the QSE and determine which CT should receive the OOME - Obtain from the QSE the MW output impact the CT’s OOME will have on the steam unit. - OOME the required CT off line. - Send an OOME equal to the amount the steam unit will produce when the CT is shut down. The intervals for both OOMEs should be the same. |
| 4 | When issuing a unit specific dispatch instruction(s) to a plant to change the output, but where all units will remain on line: - Determine what the net plant output should be. - Determine the unit(s) and MW amount per unit to be dispatched. - Send the dispatch instruction. |
| 5 | When a QSE receives a dispatch instruction that will prevent them from performing their Ancillary Service obligation, the system operator may choose to exercise one of the two following options: - Upon a QSE’s request, coordinate with the Frequency Operator for issuance of VDI to relieve the QSE from their Ancillary obligation if necessary. - Issue an instruction to release the QSE from the dispatch instruction so they can come back into compliance. |
| 6 | When notified of a SPS operation (generation disconnects from the system) which removes generation from service, if requested by the QSE, issue a VDI. - The beginning time on the VDI will be the interval that the SPS activated. - The ending time on the VDI will be the interval the SPS was restored to service. - The exception will be VDI’s will not exceed four (4) hours after the time of activation. - If the resource is a DC tie, include the name and zone of the tie. Typical Script on the VDI: “SPS operation, caused <unit name or DC tie name> to <trip or runback>”. |
| 7 | If issuing an OOME instruction on quick-start CTs that are showing “On” and “Plan MW” = 0, follow up with a Settlements only VDI stating “OOME for Quick-start” on the VDI form. |
| 8 | As time permits, forward the VDI to the Shift Supervisor. |

## 2.1.4	Three Part Communication

Procedure Purpose: To ensure that three part communication is used for all directives.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | COM-002-2 |  |  |  |
|  | R2 |  |  |  |

| Approved by: |  |  | Effective Date: September 22, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 4 |  |

| Step | Action |
| --- | --- |
| NERC: | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any one of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been place throughout the procedures as a reminder for the three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |

## 2.4.3 	Voltage Security Assessment Tool (VSAT)

Procedure Purpose: To monitor system conditions and prevent voltage collapse.

| Protocol Ref. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | EOP-001-0 R4.2 | IRO-002-1 R6, R8 | IRO-005-2 R1.2, R1.3, R1.4 | TOP-002-2 R8, R10 |
|  | TOP-004-2 R6.2 | TOP-006-1 R2 | VAR-001-1 R2, R9, R10, R12 |  |

| Approved by: |  |  | Effective Date: September 22, 2010 |  |
| --- | --- | --- | --- | --- |
| Version: | 4 | Revision: | 5 |  |

| Step | Action |
| --- | --- |
| NOTE: | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure 2.2.8 North-Houston Dynamic Stability Limit. |
| NOTE: | VSAT should be checked at least every hour, or more frequently as necessary. |
| NOTE: | To contact VSAT support, check the board in the back of PCC for the on-call personnel. |
| 1 | Determine if VSAT has run in the last 80 minutes. Reference Display: Network Online Sequence - If VSAT has not run in the last 80 minutes, contact VSAT support. - IF a South-Houston or North-Houston 345 kV circuit has a forced outage, manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) immediately and proceed to step 2. Otherwise, continue with following steps. - If any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below, it is suggested to manually rerun the whole sequence of RTNET, RTCA and RTDCP (VSA) more frequently than the periodic scheduled VSAT run and proceed to step 2. Otherwise, continue with the following steps. Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. |
| 2 | Confirm that VSAT is indicating either “Normal” or “Pending” status. NOTE: If VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status, contact VSAT support. Reference Display: Network Online Sequence |
| 3 | With VSAT in “Normal” status, determine if it indicates that a Reliability Margin may be exceeded. Reference Display: VSAT Results Page |
| NOTE: | If one of the Comanche Peak units is forced or planned to be offline, refer to Change Notice (CN) for actions. |
| NOTE: | If VSAT does not indicate a Reliability Margin is below the Reliability Margin, no further action is required. |
| 4 | Determine if the Reliability margin is less than the value located in the table below. Reference Display: Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200Mw. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. If the VSAT Reliability margin value is less than the Reliability margin value posted: |
| 5 | If the Scenario is HHGT_G-O: Instruction the QSE to raise or lower bus voltage: Typical script: “This is ERCOT operator [first and last name]. ERCOT is instructing [QSE] to [raise or lower] voltage at [specified bus] by (+ 1 or 2 kV or – 1 or 2 kV) for a target of [target kV] [QSE] please repeat this instruction back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. For all other Scenarios, proceed to Step 6. |
| 6 | Check to see if the same contingency is unsolved in RTCA. Reference Display: Contingency Analyst Solution Results If so, call VSAT support and proceed to Step 8. If not, call VSAT Support for verification and weak bus information. |
| 7 | Request the TSP in the affected area turn on capacitor banks and turn off reactors near the weak busses. |
| 8 | OOME fast ramp generators to increase generation in weak bus area. If all the online units in the weak bus area are running at maximum capacity, OOMC units that are available but offline (in weak bus area). NOTE: If an OOMC is used, call the QSE and instruct them to call and confirm their shut down before their OOMC expires and resource goes off-line. |
| 9 | Rerun VSAT with new information. Reference Display: Network Online Sequence |
| 10 | Determine if the Extra-Interface Limit pre-contingency is greater than the Reliability margin value located in the table below. Reference Displays: VSAT Results Page Click “Details” button on VSAT Results Page Reliability Margin Table. Scenario Name; Reliability Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. NOTE: If the Extra-Interface Limit pre-contingency value is greater than the Reliability margin value, no further action is required. If not, proceed to Step 13. |
| 11 | If necessary, contact VSAT Support and have them verify the results from the VSAT application on the weak bus information. |
| 12 | If it was determined that VSAT results were not an actual problem. No further action is required and the system may be restored back to the original state. |
| 13 | Determine if there are more units available in the affected area. If there are more units available in the affected area, repeat steps 7, 8, 9, and 10. |
| NOTE: | If there are no more units available in the area, proceed to step 14. |
| 14 | Ensure that the OPS Support Engineering group has been contacted to devise a mitigation plan. |